## Prototype Inputs
Each row contains the inputs for a specific building type/climate zone/vintage combination | [15 empty] | SmallOffice Exterior Lights
SmallOffice Exterior Lights Always On
Template | Climate Zone | Building Type | CHW Pumping Type | Chiller Cooling Type | Chiller Condenser Type | Chiller Compressor Type | Chiller Capacity Guess (Tons) | PSZAC Cooling Type | PSZAC Heating Type | PSZAC Fan Type | PSZAC Supplemental Heating Type | PSZAC Operation Schedule | PSZAC OA Damper Schedule | HX | Occ Sensing Exterior Lighting Power | Occ Sensing Exterior Lighting Schedule | NonDimming Exterior Lighting Power | NonDimming Exterior Lighting Schedule | Main Water Heater Volume (gal) | Main Water Heater Fuel | Main Water Heater Capacity (Btu/hr) | Main Service Water Temperature (F) | Main Service Water FlowRate Schedule | Main Service Water Peak FlowRate (gal/min) | Main Water Use Temperature (F) | Main Service Water Temperature at Fixture (F) | Main Service Water Pump Head (Pa) | Main Service Water Pump Motor Efficiency (%) | Laundry Water Heater Volume (gal) | Laundry Water Heater Fuel | Laundry Water Heater Capacity (Btu/hr) | Laundry Service Water Temperature (F) | Laundry Service Water FlowRate Schedule | Laundry Service Water Peak FlowRate (gal/min) | Laundry Water Use Temperature (F) | Laundry Service Water Temperature at Fixture (F) | Laundry Service Water Pump Head (Pa) | Laundry Service Water Pump Motor Efficiency (%) | Booster Water Heater Volume (gal) | Booster Water Heater Fuel | Booster Water Heater Capacity (Btu/hr) | Booster Inlet Water Temperature (F) | Booster Service Water FlowRate Schedule | Booster Service Water Peak FlowRate (gal/min) | Booster Water Use Temperature (F) | Booster Water Temperature (F) | Typical Heating Setpoint | Typical Cooling Setpoint | PTAC Cooling Type | PTAC Heating Type | PTAC Fan Type | PTAC Operation Schedule | PTAC OA Damper Schedule | SAC Cooling Type | SAC Heating Type | SAC Fan Type | SAC Operation Schedule | SAC OA Damper Schedule | UnitHeater Heating Type | UnitHeater Fan Type | UnitHeater Fan Control Type | VAV Operation Schedule | VAV OA Damper Schedule | Building Elevator Power | Building Elevator Schedule
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
90.1-2010 | ASHRAE 169-2006-2A | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | TRUE | 8427.85 | SchoolSecondary Exterior_lighting_schedule_b | 353.47 | SchoolSecondary Exterior_lighting_schedule_a | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | [12 empty] | 6 | Electricity | 64831 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [15 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
90.1-2010 | ASHRAE 169-2006-3B | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | TRUE | 8427.85 | SchoolSecondary Exterior_lighting_schedule_b | 353.47 | SchoolSecondary Exterior_lighting_schedule_a | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | [12 empty] | 6 | Electricity | 64831 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [15 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
90.1-2010 | ASHRAE 169-2006-4A | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | TRUE | 8427.85 | SchoolSecondary Exterior_lighting_schedule_b | 353.47 | SchoolSecondary Exterior_lighting_schedule_a | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | [12 empty] | 6 | Electricity | 64831 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [15 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | SecondarySchool | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper |  |  |  | 21874 | SecondarySchool Exterior Lights Always On | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
90.1-2010 | ASHRAE 169-2006-5A | SecondarySchool | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | TRUE | 8427.85 | SchoolSecondary Exterior_lighting_schedule_b | 353.47 | SchoolSecondary Exterior_lighting_schedule_a | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | 7.63 | 140 | 140 | [12 empty] | 6 | Electricity | 64831 | 140 | SchoolSecondary BLDG_SWH_SCH | 23.7 | 180 | 180 | [15 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
90.1-2010 | ASHRAE 169-2006-2A | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | FALSE | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 | [20 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
90.1-2010 | ASHRAE 169-2006-3B | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | FALSE | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 | [20 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
90.1-2010 | ASHRAE 169-2006-4A | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | FALSE | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 | [20 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | SmallOffice | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | FALSE |  |  | 2766 | SmallOffice Exterior Lights Always On | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.05 | 110 | 110 | [20 empty] | Small Office HtgSetp | Small Office ClgSetp
90.1-2010 | ASHRAE 169-2006-5A | SmallOffice | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched | FALSE | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | 0.064 | 120 | 131 | [20 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | SmallHotel | [14 empty] | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | SmallHotel | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | FALSE |  |  | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-2A | SmallHotel | [14 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
90.1-2004 | ASHRAE 169-2006-2A | SmallHotel | [14 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | SmallHotel | [14 empty] | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | SmallHotel | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | FALSE |  |  | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-3B | SmallHotel | [14 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
90.1-2004 | ASHRAE 169-2006-3B | SmallHotel | [14 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | SmallHotel | [14 empty] | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | SmallHotel | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | FALSE |  |  | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-4A | SmallHotel | [14 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
90.1-2004 | ASHRAE 169-2006-4A | SmallHotel | [14 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | SmallHotel | [14 empty] | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | SmallHotel | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | FALSE |  |  | 16715 | SmallHotel Exterior Lights | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | 3.361 | 110 | 110 | 179352 | 0.9 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 1.125 | 140 | 140 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [5 empty] | Electric | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-5A | SmallHotel | [14 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
90.1-2004 | ASHRAE 169-2006-5A | SmallHotel | [14 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | 1.852 | 140 | 140 | 29891 | 0.85 | 200 | Natural Gas | 200000 | 140 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | [10 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
90.1-2004 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2007 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2013 | ASHRAE 169-2006-2A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
90.1-2004 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2007 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2013 | ASHRAE 169-2006-3B | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
90.1-2004 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2007 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2013 | ASHRAE 169-2006-4A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.7 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper |  |  |  | 10519 | PrimarySchool Exterior Lights Always On | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | 2.6 | 110 | 110 | 1 | 1 | [33 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper
90.1-2004 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.67 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2007 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.67 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.67 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
90.1-2013 | ASHRAE 169-2006-5A | PrimarySchool | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | TRUE | 3340.3 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | 1.67 | 140 | 140 | 29891 | 0.3 | [10 empty] | 6 | Electricity | 20473 | 140 | SchoolPrimary BLDG_SWH_SCH | 1 | 180 | 180 | [15 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | MediumOffice | [11 empty] | FALSE |  |  | 14385 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | MediumOffice | [11 empty] | FALSE |  |  | 17809 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
90.1-2010 | ASHRAE 169-2006-2A | MediumOffice | [11 empty] | FALSE | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a | 100 | Natural Gas | 100000 | 140 | Medium Office Bldg Swh | 0.0567 | 140 | 131 | 29891 | 0.3 | [18 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | MediumOffice | [11 empty] | FALSE |  |  | 14385 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | MediumOffice | [11 empty] | FALSE |  |  | 17809 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
90.1-2010 | ASHRAE 169-2006-3B | MediumOffice | [11 empty] | FALSE | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a | 100 | Natural Gas | 100000 | 140 | Medium Office Bldg Swh | 0.0567 | 140 | 131 | 29891 | 0.3 | [18 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | MediumOffice | [11 empty] | FALSE |  |  | 14385 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | MediumOffice | [11 empty] | FALSE |  |  | 17809 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
90.1-2010 | ASHRAE 169-2006-4A | MediumOffice | [11 empty] | FALSE | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a | 100 | Natural Gas | 100000 | 140 | Medium Office Bldg Swh | 0.0567 | 140 | 131 | 29891 | 0.3 | [18 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | MediumOffice | [11 empty] | FALSE |  |  | 14385 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | MediumOffice | [11 empty] | FALSE |  |  | 17809 | SmallOffice Exterior Lights Always On | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | 0.16484 | 110 | 110 | 179352 | 0.85 | [18 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [13 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 32109.8901 | Medium Office BLDG ELEVATORS
90.1-2010 | ASHRAE 169-2006-5A | MediumOffice | [11 empty] | FALSE | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a | 100 | Natural Gas | 100000 | 140 | Medium Office Bldg Swh | 0.0567 | 140 | 131 | 29891 | 0.3 | [18 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 32109.8901 | Medium Office BLDG ELEVATORS
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
90.1-2010 | ASHRAE 169-2006-3B | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 900 | Natural Gas | 900000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 140 |  | 140 | [11 empty] | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | [15 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
90.1-2010 | ASHRAE 169-2006-4A | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 900 | Natural Gas | 900000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 140 |  | 140 | [11 empty] | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | [15 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
90.1-2010 | ASHRAE 169-2006-5A | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 900 | Natural Gas | 900000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 140 |  | 140 | [11 empty] | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | [15 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | LargeHotel | const_pri | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 1200 | Natural Gas | 3600 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 110 |  | 110 | [34 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
90.1-2010 | ASHRAE 169-2006-2A | LargeHotel | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [6 empty] | TRUE | 8427.85 | HotelLarge Exterior_Ltg_Sch | 353.47 | HotelLarge Exterior_Ltg_Sch | 900 | Natural Gas | 900000 | 140 | HotelLarge BLDG_SWH_SCH | 4.4 | 140 |  | 140 | [11 empty] | 6 | Electricity | 27297 | 140 | HotelLarge BLDG_SWH_SCH | 1.33 | 180 | 180 | [15 empty] | HotelLarge HVACOperationSchd | HotelLarge HVACOperationSchd
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-2A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | TRUE | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | [18 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-3B | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | TRUE | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | [18 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-4A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | TRUE | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | [18 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | [9 empty] | 21874 | Always On | 792 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | 7.18 | 110 | 110 | [35 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
90.1-2010 | ASHRAE 169-2006-5A | LargeOffice | const_pri | AirCooled | WithCondenser |  | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | TRUE | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | 0.58 | 140 | 140 | 29891 | 0.3 | [18 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [13 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-2A | Warehouse | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE | 91 | Warehouse Exterior_lighting_schedule_b | 6123.42 | Warehouse Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 | [20 empty] | Warehouse HtgSetp BulkStorage | Warehouse CLGSETP_SCH | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-3B | Warehouse | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE | 91 | Warehouse Exterior_lighting_schedule_b | 6123.42 | Warehouse Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 | [20 empty] | Warehouse HtgSetp BulkStorage | Warehouse CLGSETP_SCH | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-4A | Warehouse | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE | 91 | Warehouse Exterior_lighting_schedule_b | 6123.42 | Warehouse Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 | [20 empty] | Warehouse HtgSetp BulkStorage | Warehouse CLGSETP_SCH | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | Warehouse | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-5A | Warehouse | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | FALSE | 91 | Warehouse Exterior_lighting_schedule_b | 6123.42 | Warehouse Exterior_lighting_schedule_a | 40 | Electricity | 40000 | 140 |  |  | 120 | 131 | [20 empty] | Warehouse HtgSetp BulkStorage | Warehouse CLGSETP_SCH | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-2A | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-3B | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-4A | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | RetailStandalone | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE |  |  | 10958 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | Retail HtgSetp | Retail ClgSetp | [10 empty] | Gas | ConstantVolume | OnOff
90.1-2010 | ASHRAE 169-2006-5A | RetailStandalone | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | FALSE | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [10 empty] | Gas | ConstantVolume | OnOff
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
90.1-2010 | ASHRAE 169-2006-2A | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
90.1-2010 | ASHRAE 169-2006-3B | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
90.1-2010 | ASHRAE 169-2006-4A | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | RetailStripmall | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE |  |  | 10958 | RetailStripmall Exterior_Lgt_ALWAYS_ON | 40 | Natural Gas | 2883000 | 140 |  |  | 110 | 110 | [20 empty] | StripMall HtgSetp | StripMall ClgSetp
90.1-2010 | ASHRAE 169-2006-5A | RetailStripmall | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type3_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | FALSE | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a | 40 | Natural Gas | 40000 | 140 |  |  | 120 | 131 | [20 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK

## Chillers
Each row represents the efficiency standards for a specificy type of chiller
Template | Cooling Type | Condenser Type | Compressor Type | Absorption Type | Minimum Capacity (Tons) | Maximum Capacity (Tons) | Minimum Full Load Efficiency (kW/ton) | Minimum Integrated Part Load Value (kW/ton) | CAPFT | EIRFT | EIRFPLR | Notes
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.303 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 150 | 299.99 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  | 300 | 9999 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 0 | 149.99 | 1.303 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 150 | 299.99 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  | 300 | 9999 | 1.332 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.884 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.852 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.782 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.688 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.852 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.782 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.688 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.776 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.713 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.635 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled |  |  | Single Effect | 0 | 9999 | 6.395 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.097 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.589 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.589 |  |  |  |  | From DOE Reference Buildings
DOE Ref 1980-2004 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.407 | 1.407 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.135 | 1.099 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.926 | 0.902 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.837 | 0.782 |  |  |  | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.676 | 0.664 |  |  |  | From 90.1-1989
90.1-2004 | AirCooled | WithCondenser |  |  | 0 | 9999 | 1.256 | 1.153
90.1-2004 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.135 | 1.019
90.1-2004 | WaterCooled |  | Reciprocating |  | 0 | 149.99 | 0.837 | 0.696
90.1-2004 | WaterCooled |  | Reciprocating |  | 150 | 9999 | 0.837 | 0.696
90.1-2004 | WaterCooled |  | Rotary Screw |  | 0 | 149.99 | 0.79 | 0.676
90.1-2004 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.718 | 0.628
90.1-2004 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.639 | 0.572
90.1-2004 | WaterCooled |  | Scroll |  | 0 | 149.99 | 0.79 | 0.676
90.1-2004 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.718 | 0.628
90.1-2004 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.639 | 0.572
90.1-2004 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.703 | 0.67
90.1-2004 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.634 | 0.596
90.1-2004 | WaterCooled |  | Centrifugal |  | 300 | 9999 | 0.577 | 0.55
90.1-2004 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
90.1-2004 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
90.1-2004 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2004 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517
90.1-2010 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithoutCondenser |  |  | 0 | 9999 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | WaterCooled |  | Reciprocating |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 0 | 74.99 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 75 | 149.99 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  | 300 | 9999 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.634 | 0.596 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.634 | 0.596 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 300 | 599.99 | 0.576 | 0.549 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  | 600 | 9999 | 0.57 | 0.539 |  |  |  | Path A Minimum Efficiencies
90.1-2010 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
90.1-2010 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
90.1-2010 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2010 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517
90.1-2013 | AirCooled | WithCondenser |  |  | 0 | 149.99 | 1.188 | 0.876
90.1-2013 | AirCooled | WithCondenser |  |  | 150 | 9999 | 1.188 | 0.857
90.1-2013 | AirCooled | WithoutCondenser |  |  | 0 | 149.99 | 1.188 | 0.876
90.1-2013 | AirCooled | WithoutCondenser |  |  | 150 | 9999 | 1.188 | 0.857
90.1-2013 | WaterCooled |  | Reciprocating |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Reciprocating |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Reciprocating |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Reciprocating |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Reciprocating |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Scroll |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Scroll |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Scroll |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Scroll |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Scroll |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Rotary Screw |  | 0 | 74.99 | 0.75 | 0.6
90.1-2013 | WaterCooled |  | Rotary Screw |  | 75 | 149.99 | 0.72 | 0.56
90.1-2013 | WaterCooled |  | Rotary Screw |  | 150 | 299.99 | 0.66 | 0.54
90.1-2013 | WaterCooled |  | Rotary Screw |  | 300 | 599.99 | 0.61 | 0.52
90.1-2013 | WaterCooled |  | Rotary Screw |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Centrifugal |  | 0 | 149.99 | 0.61 | 0.55
90.1-2013 | WaterCooled |  | Centrifugal |  | 150 | 299.99 | 0.61 | 0.55
90.1-2013 | WaterCooled |  | Centrifugal |  | 300 | 399.99 | 0.56 | 0.52
90.1-2013 | WaterCooled |  | Centrifugal |  | 400 | 599.99 | 0.56 | 0.5
90.1-2013 | WaterCooled |  | Centrifugal |  | 600 | 9999 | 0.56 | 0.5
90.1-2013 | AirCooled |  |  | Single Effect | 0 | 9999 | 5.862
90.1-2013 | WaterCooled |  |  | Single Effect | 0 | 9999 | 5.024
90.1-2013 |  |  |  | Double Effect Indirect Fired | 0 | 9999 | 3.517 | 3.35
90.1-2013 |  |  |  | Double Effect Direct Fired | 0 | 9999 | 3.517 | 3.517

## Unitary ACs
Each row represents the efficiency standards for a specificy type of chiller
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Seasonal Energy Efficiency Ratio (SEER) | Minimum Energy Efficiency Ratio (EER) | Minimum Integrated Part Load Value (kW/ton) | Minimum Integrated Energy Efficiency Ratio (IEER) | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 11.09 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 0 | 64999 | 11.09 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 11.06 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 0 | 64999 | 11.06 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 9.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 9.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 65000 | 134999 |  | 9.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 9.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.28 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.28 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.28 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.28 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 8.92 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 8.92 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 240000 | 759999 |  | 8.92 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 8.92 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 8.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 8.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 8.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 8.63 |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 0 | 64999 | 10 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 10 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 9.7 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 9.7 |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 65000 | 134999 |  | 8.9 | 8.3 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 8.9 | 8.3 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 8.9 | 8.3 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 8.9 | 8.3 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 135000 | 759999 |  | 8.5 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 759999 |  | 8.5 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 135000 | 759999 |  | 8.5 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 759999 |  | 8.5 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 8.2 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 8.2 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 8.2 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 8.2 | 7.5 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 10
90.1-2004 | AirCooled | All Other | Split System | 0 | 64999 | 10
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 9.7
90.1-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 10.3
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 10.3
90.1-2004 | AirCooled | All Other | Split System | 65000 | 134999 |  | 10.1
90.1-2004 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 10.1
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.7
90.1-2004 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.5
90.1-2004 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.5
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 9.5 | 9.7
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 9.5 | 9.7
90.1-2004 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.3 | 9.5
90.1-2004 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.3 | 9.5
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2004 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9 | 9.2
90.1-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9 | 9.2
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13
90.1-2007 | AirCooled | All Other | Split System | 0 | 64999 | 13
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 13
90.1-2007 | AirCooled | All Other | Single Package | 0 | 64999 | 13
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 10.3
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 10.3
90.1-2007 | AirCooled | All Other | Split System | 65000 | 134999 |  | 10.1
90.1-2007 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 10.1
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 9.7
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 9.7
90.1-2007 | AirCooled | All Other | Split System | 135000 | 239999 |  | 9.5
90.1-2007 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 9.5
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 9.5 | 9.7
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 9.5 | 9.7
90.1-2007 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.3 | 9.5
90.1-2007 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.3 | 9.5
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.2 | 9.4
90.1-2007 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9 | 9.2
90.1-2007 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9 | 9.2
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | DX Coil Cap-FF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC:1_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2010 | AirCooled | All Other | Split System | 0 | 64999 | 13 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | DX Coil Cap-FF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC:1_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 13 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | DX Coil Cap-FF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC:1_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2010 | AirCooled | All Other | Single Package | 0 | 64999 | 13 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | DX Coil Cap-FF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC:1_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 11.2 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 11.2 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 65000 | 134999 |  | 11 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 11 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 11 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 11 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 135000 | 239999 |  | 10.8 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 10.8 |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 10 |  | 9.7 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 10 |  | 9.7 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.8 |  | 9.7 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.8 |  | 9.7 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.7 |  | 9.4 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.7 |  | 9.4 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9.5 |  | 9.2 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9.5 |  | 9.2 | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 13
90.1-2013 | AirCooled | All Other | Split System | 0 | 64999 | 13
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 14
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 14
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 |  | 11.2 |  | 11.4
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 |  | 11.2 |  | 11.4
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 |  | 11 |  | 11.2
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 |  | 10.8 |  | 11
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 |  | 10.8 |  | 11
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 |  | 10 |  | 10.1
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 |  | 10 |  | 10.1
90.1-2013 | AirCooled | All Other | Split System | 240000 | 759999 |  | 9.8 |  | 9.9
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 759999 |  | 9.8 |  | 9.9
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 |  | 9.7 |  | 9.8
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 |  | 9.7 |  | 9.8
90.1-2013 | AirCooled | All Other | Split System | 760000 | 9999999 |  | 9.5 |  | 9.6
90.1-2013 | AirCooled | All Other | Single Package | 760000 | 9999999 |  | 9.5 |  | 9.6

## Heat Pumps
Each row represents the efficiency standards for a specificy type of chiller
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Seasonal Efficiency (SEER) | Minimum Full Load Efficiency (EER) | Minimum IPLV | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 0 | 9999999 | 13 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR

## Boilers
Each row represents the efficiency standards for a specific type of boiler
Template | Fluid Type | Fuel Type | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Minimum Annual Fuel Utilization Efficiency (AFUE) | Minimum Thermal Efficiency (%) | Minimum Combustion Efficiency (%) | EFFFPLR | Notes
DOE Ref Pre-1980 | Hot Water | Gas | 0 | 299999 |  | 0.73 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas | 300000 | 9999999999 |  | 0.74 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas | 250000000 | 9999999999 |  | 0.76 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref 1980-2004 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler Constant Efficiency Curve | From 90.1-1989
DOE Ref 1980-2004 | Hot Water | Gas | 300000 | 249999999 |  |  | 0.8 | Boiler Constant Efficiency Curve | From 90.1-1989
90.1-2004 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas | 300000 | 249999999 |  | 0.75 |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.8 | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2007 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas | 300000 | 249999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2010 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas | 300000 | 249999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2013 | Hot Water | Gas | 0 | 299999 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 300000 | 999999 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 1000000 | 249999999 |  | 0.8 |  | Boiler with Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas | 250000000 | 9999999999 |  |  | 0.82 | Boiler with Minimum Turndown | From 90.1-2013

## Curve Biquadratics
Each row represents a biquadratic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | coeff_5 | coeff_6 | min_x | max_x | min_y | max_y | notes
WaterCooled_PositiveDisplacement_Chiller_2004_CAPFT | 0.90612 | 0.029227 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2004_EIRFT | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | 0.37731 | -0.022903 | 0.0016504 | 0.011816 | 0.0004345 | -0.0010132 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_CAPFT | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_EIRFT | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | 0.53623 | 0.005581 | -0.0013654 | 0.048897 | -0.0012018 | 0.0010523 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | 1.0822 | 0.0042977 | -0.0013182 | -0.026078 | 0.0008256 | -0.0006013 | 5 | 10 | 17.78 | 46.11 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2004_CAPFT | 1.0434 | 0.040708 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2004_EIRFT | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_CAPFT | 1.0434 | 0.040707 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_EIRFT | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 | 5 | 10 | 12.7 | 51.67 | Based on Dick Lord's study dated January 17, 2010.
ChillerCentCapFT | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 | 5 | 10 | 24 | 35 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
ChillerCentEIRFT | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 | 5 | 10 | 24 | 35 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
DOE Ref DX Clg Coil Cool-Cap-fT | 0.97121 | -0.015276 | 0.0014435 | -0.00039321 | -6.8364e-06 | -0.0002906 | -100 | 100 | -100 | 100 | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-EIR-fT | 0.28687 | 0.023902 | -0.00081065 | 0.013459 | 0.00033894 | -0.000487 | -100 | 100 | -100 | 100 | From DOE Pre-1980 Reference Building
HPACCoolCapFT | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 | 12.7778 | 23.8889 | 21.1111 | 46.1111
HPACCOOLEIRFT | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 | 12.7778 | 23.8889 | 21.1111 | 46.1111
PSZ-AC DX Unitary Package EIRFT | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 | 12.7778 | 23.8889 | 21.1111 | 46.1111 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall,SchoolPrimary
PSZ-AC DX Coil EIR-FT | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 | 12.7778 | 23.8889 | 23.8889 | 46.1111 | From PNNL Prototype Buildings HotelSmall, Warehouse
PTACHPACEIRFT | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 | 12.7778 | 23.8889 | 18.3 | 46.1111 | From DOE Reference Buildings SmallHotel
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFT | -0.53616 | 0.10514 | -0.0017266 | 0.014985 | 0.00065995 | -0.0017385 | 16.5556 | 22.1111 | 23.7778 | 47.66 | From PNNL Prototype Buildings OfficeMedium
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | 0.42415 | 0.04426 | -0.00042 | 0.00333 | -8e-05 | -0.00021 | 17 | 22 | 29 | 46 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
WC_PD_2010_PB_EIRFT | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype OfficeLarge
PSZ-AC_Unitary_PackagecoolCapFT | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 | 12.7778 | 23.8889 | 21.1111 | 46.1111 | From PNNL Prototype Buildings RetailStandalone, RetailStripMall, SchoolPrimary
WC_PD_2010_PB_CAPFT | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype OfficeLarge
WC_PD_2004_CAPFT | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 | 5 | 10 | 17.78 | 46.11 | From PNNL Prototype Hospital
PSZ-AC_CoolCStandard10Ton_EIRFT | 1.2365 | -0.02431 | 0.00057 | -0.01434 | 0.00063 | -0.00038 | 17 | 22 | 29 | 46 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
PSZ-Fine Storage DX Coil Cap-FT | 0.94259 | 0.0095433 | 0.00068377 | -0.011043 | 5.249e-06 | -9.72e-06 | 12.7778 | 23.8889 | 23.8889 | 46.1111 | From PNNL Prototype Buildings HotelSmall, Warehouse

## Curve Bicubics
Each row represents a bicubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | coeff_5 | coeff_6 | coeff_7 | coeff_8 | coeff_9 | coeff_10 | min_x | max_x | min_y | max_y | notes
WaterCooled_PositiveDisplacement_Chiller_LT75_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT300_2004_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathA_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathB_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010.
ChillerCentEIRPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all WaterCooled Chillers

## Curve Quadratics
Each row represents a bicubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | min_x | max_x | notes
AirCooled_Chiller_LT150_2004_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_GT150_2004_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_LT150_2010_PathA_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_GT150_2010_PathA_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | 0.141 | 0.655 | 0.203 | 0 | 1 | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all AirCooled Chillers
DOE Ref DX Clg Coil Cool-PLF-fPLR | 0.9095 | 0.098648 | -0.0081949 | 0 | 1
HPACCoolCapFFF | 0.8 | 0.2 | 0 | 0.5 | 1.5
HPACCOOLEIRFFF | 1.156 | -0.1816 | 0.0256 | 0.5 | 1.5
HPACCOOLPLFFPLR | 0.85 | 0.15 | 0 | 0 | 1
PSZ-AC_Unitary_PackagecoolPLR | 0.75 | 0.25 | 0 | 0 | 1 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR | 0.771 | 0.229 | 0 | 0 | 1 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
AHU-1_CoolCStandard10Ton_CapFF | 0.77136 | 0.34053 | -0.11088 | 0.75918 | 1.1388 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
DX Coil Cap-FF | 0.8 | 0.2 | 0 | 0.5 | 1.5 | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, OfficeSmall, RetailStandAlone, RetailStripmall, SchoolPrimary, Warehouse
Split DX Coil EIR-FF | 1.1552 | -0.1808 | 0.0256 | 0.5 | 1.5 | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, Warehouse
Cool-PLF-fPLR | 0.9095 | 0.098648 | -0.0081949 | 0 | 1 | From PNNL Prototype FullServiceRestaurant
PSZ-AC:1_Unitary_PackagecoolEIRFFF | 1.156 | -0.1816 | 0.0256 | 0.5 | 1.5 | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
Measured_CoolCStandard10Ton_EIRFFF | 1.192 | -0.1917 | 0 | 0.776 | 1.197 | From PNNL Prototype FullServiceRestaurant
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFFF | 1.1952 | -0.30614 | 0.11097 | 0.75 | 1.25 | From PNNL OfficeMedium
CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | 1.2055 | -0.32953 | 0.12308 | 0.75918 | 1.1388 | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary

## Curve Cubics
Each row represents a cubic curve used to describe HVAC component performance
Name | coeff_1 | coeff_2 | coeff_3 | coeff_4 | min_x | max_x | notes
DOE Ref DX Clg Coil Cool-EIR-fFlow | 1 | 0 | 0 | 0 | -100 | 100 | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-CAP-fFlow | 1 | 0 | 0 | 0 | -100 | 100 | From DOE Pre-1980 Reference Building
Boiler with Minimum Turndown | 0.7791 | 1.4745 | -2.5795 | 1.3467 | 0 | 1.3 | From Regression of Prototype Building EMS
Boiler with No Minimum Turndown | 0.7463 | 1.3196 | -2.2154 | 1.1674 | 0 | 1.3 | From Regression of Prototype Building EMS
Boiler Constant Efficiency Curve | 1 | 0 | 0 | 0 | 0 | 1 | From DOE Reference Building

## Motors
Each row represents the efficiency standards for a specificy type of chiller
Template | Number of Poles | Type | Synchronous Speed (RPM) | Minimum Capacity (HP) | Maximum Capacity (HP) | Nominal Full Load Efficiency (%) | Notes
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 0 | 0.99 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1 | 1.49 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 2 | 2.99 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 3 | 4.99 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 5 | 7.49 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 10 | 14.99 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 15 | 19.99 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 20 | 24.99 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 25 | 29.99 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 30 | 39.99 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 40 | 49.99 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 50 | 59.99 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 60 | 74.99 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 75 | 99.99 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 100 | 124.99 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 125 | 149.99 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 150 | 199.99 | 95% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 0 | 0.99 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1 | 1.49 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 2 | 2.99 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 3 | 4.99 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 5 | 7.49 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 10 | 14.99 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 15 | 19.99 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 20 | 24.99 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 25 | 29.99 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 30 | 39.99 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 40 | 49.99 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 50 | 59.99 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 60 | 74.99 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 75 | 99.99 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 100 | 124.99 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 125 | 149.99 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 150 | 199.99 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 0 | 0.99 | 82.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 1 | 1.49 | 82.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 2 | 2.99 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 3 | 4.99 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 5 | 7.49 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 10 | 14.99 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 15 | 19.99 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 20 | 24.99 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 25 | 29.99 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 30 | 39.99 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 40 | 49.99 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 50 | 59.99 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 60 | 74.99 | 93.6% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 75 | 99.99 | 94.1% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 100 | 124.99 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 125 | 149.99 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 150 | 199.99 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 0 | 0.99 | 82.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 1 | 1.49 | 82.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 2 | 2.99 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 3 | 4.99 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 5 | 7.49 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 10 | 14.99 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 15 | 19.99 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 20 | 24.99 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 25 | 29.99 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 30 | 39.99 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 40 | 49.99 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 50 | 59.99 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 60 | 74.99 | 93.6% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 75 | 99.99 | 94.1% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 100 | 124.99 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 125 | 149.99 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 150 | 199.99 | 95% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2007 Table 10.8
90.1-2010 | 4 | Enclosed | 1800 | 0 | 0.99 | 85.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 1 | 1.49 | 85.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 2 | 2.99 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 3 | 4.99 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 5 | 7.49 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 10 | 14.99 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 15 | 19.99 | 92.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 20 | 24.99 | 93% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 25 | 29.99 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 30 | 39.99 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 40 | 49.99 | 94.1% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 50 | 59.99 | 94.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 60 | 74.99 | 95% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 75 | 99.99 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 100 | 124.99 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 125 | 149.99 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 150 | 199.99 | 95.8% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 200 | 249.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 250 | 299.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 300 | 349.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 350 | 399.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 400 | 449.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 450 | 499.99 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 500 | 9999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2013 | 4 | Enclosed | 1800 | 0 | 0.99 | 85.5%
90.1-2013 | 4 | Enclosed | 1800 | 1 | 1.49 | 85.5%
90.1-2013 | 4 | Enclosed | 1800 | 1.5 | 1.99 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 2 | 2.99 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 3 | 4.99 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 5 | 7.49 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 7.5 | 9.99 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 10 | 14.99 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 15 | 19.99 | 92.4%
90.1-2013 | 4 | Enclosed | 1800 | 20 | 24.99 | 93%
90.1-2013 | 4 | Enclosed | 1800 | 25 | 29.99 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 30 | 39.99 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 40 | 49.99 | 94.1%
90.1-2013 | 4 | Enclosed | 1800 | 50 | 59.99 | 94.5%
90.1-2013 | 4 | Enclosed | 1800 | 60 | 74.99 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 75 | 99.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 100 | 124.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 125 | 149.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 150 | 199.99 | 95.8%
90.1-2013 | 4 | Enclosed | 1800 | 200 | 249.99 | 96.2%
90.1-2013 | 4 | Enclosed | 1800 | 250 | 299.99 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 300 | 349.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 350 | 399.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 400 | 449.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 450 | 499.99 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 500 | 9999 | 95.4%

## Schedules
Each row represents the efficiency standards for a specificy type of chiller
Day Type choices: Default, Wkdy, Wknd, Mon, Tue, Wed, Thu, Fri, Sat, Sun, WntrDsn, SmrDsn, Hol
Name | Category | Units | Day Types | Start Date | End Date | Type | Hr 1 | Hr 2 | Hr 3 | Hr 4 | Hr 5 | Hr 6 | Hr 7 | Hr 8 | Hr 9 | Hr 10 | Hr 11 | Hr 12 | Hr 13 | Hr 14 | Hr 15 | Hr 16 | Hr 17 | Hr 18 | Hr 19 | Hr 20 | Hr 21 | Hr 22 | Hr 23 | Hr 24 | Notes
Always Off | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Always On | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
FullServiceRestaurant Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
FullServiceRestaurant Bldg Equip | Equipment | Dimensionless | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
FullServiceRestaurant Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
FullServiceRestaurant Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
FullServiceRestaurant Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
FullServiceRestaurant Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
FullServiceRestaurant Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
FullServiceRestaurant Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
FullServiceRestaurant Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
FullServiceRestaurant Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
FullServiceRestaurant Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
FullServiceRestaurant Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
FullServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
FullServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
FullServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
FullServiceRestaurant ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
FullServiceRestaurant ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
FullServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
FullServiceRestaurant Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
FullServiceRestaurant Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
FullServiceRestaurant Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
FullServiceRestaurant Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
FullServiceRestaurant Gas Equip | Equipment | Dimensionless | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
FullServiceRestaurant Gas Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
FullServiceRestaurant Gas Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
FullServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
FullServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
FullServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19
FullServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
FullServiceRestaurant Infil Half On | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
FullServiceRestaurant Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Hospital Bldg ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
Hospital Bldg ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Hospital Bldg ClgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25
Hospital BLDG ELEVATORS | Elevator | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital BLDG ELEVATORS | Elevator | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital BLDG ELEVATORS | Elevator | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital Bldg Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
Hospital Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3
Hospital Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
Hospital Bldg HtgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Hospital Bldg HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Hospital Bldg HtgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3
Hospital Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
Hospital Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
Hospital Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Hospital Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Hospital Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Hospital Critical ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22.2
Hospital Critical Equip | Equipment | Dimensionless | Default¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5
Hospital Critical Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3
Hospital Critical HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1
Hospital Critical Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5
Hospital Critical Occ | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4
Hospital Infil Quarter On | Infiltration | Dimensionless | Default¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Constant | 0.25
Hospital Infil Quarter On | Infiltration | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Kitchen ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30
Hospital Kitchen ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Hospital Kitchen ClgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 30
Hospital Kitchen Exhaust | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Hospital Kitchen Exhaust | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital Kitchen Exhaust | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital Kitchen Gas | Equipment | Dimensionless | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
Hospital Kitchen Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital Kitchen Gas | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
Hospital Kitchen HtgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Hospital Kitchen HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Hospital Kitchen HtgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 15.6
Hospital OR ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
Hospital OR HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3
Hospital Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Large Office Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Large Office BLDG ELEVATORS | Elevator | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
Large Office Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4
Large Office Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Large Office Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Large Office Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3
Large Office Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Large Office Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05
Large Office Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Large Office Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Large Office Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05
Large Office Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Large Office Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05
Large Office Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Large Office Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
Large Office Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large Office ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
Large Office ClgSetp | Thermostat Setpoint | Temperature | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7
Large Office ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Large Office Clothing | Clothing | Unknown | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Large Office Clothing | Clothing | Unknown | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Large Office Clothing | Clothing | Unknown | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Large Office Clothing | Clothing | Unknown | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Large Office HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
Large Office HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Large Office HtgSetp | Thermostat Setpoint | Temperature | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6
Large Office HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Large Office Infil Quarter On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
Large Office Infil Quarter On | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Large Office Infil Quarter On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 1
Large Office Work Eff | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
LargeHotel BLDG ELEVATORS | Elevator | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
LargeHotel Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
LargeHotel Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
LargeHotel Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
LargeHotel Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
LargeHotel Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
LargeHotel Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
LargeHotel Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
LargeHotel Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
LargeHotel Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
LargeHotel ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LargeHotel Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
LargeHotel Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
LargeHotel Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
LargeHotel Corridor ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
LargeHotel Corridor HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
LargeHotel GuestRoom ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
LargeHotel GuestRoom Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
LargeHotel GuestRoom Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel GuestRoom Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel GuestRoom Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
LargeHotel GuestRoom HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
LargeHotel GuestRoom Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65
LargeHotel GuestRoom Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel GuestRoom Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel GuestRoom Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
LargeHotel HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
LargeHotel Infil Quarter On | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
LargeHotel Kitchen ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
LargeHotel Kitchen Equip | Equipment | Dimensionless | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
LargeHotel Kitchen Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Kitchen Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
LargeHotel Kitchen Exhaust | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
LargeHotel Kitchen Gas | Equipment | Dimensionless | Default¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
LargeHotel Kitchen Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Kitchen Gas | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
LargeHotel Kitchen HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
LargeHotel LaundryRoom Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LargeHotel LaundryRoom Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel LaundryRoom Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel LaundryRoom Gas | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LargeHotel LaundryRoom Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel LaundryRoom Gas | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Lobby Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
LargeHotel Lobby Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
LargeHotel Lobby Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
LargeHotel Lobby Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
LargeHotel Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Medium Office Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Medium Office BLDG ELEVATORS | Elevator | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0
Medium Office BLDG ELEVATORS | Elevator | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office BLDG ELEVATORS | Elevator | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Medium Office Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4
Medium Office Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Medium Office Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Medium Office Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3
Medium Office Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Medium Office Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05
Medium Office Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Medium Office Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Medium Office Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05
Medium Office Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Medium Office Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05
Medium Office Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Medium Office Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
Medium Office Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office Bldg Swh | Service Water Heating | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Medium Office Bldg Swh | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
Medium Office Bldg Swh | Service Water Heating | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Medium Office ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
Medium Office ClgSetp | Thermostat Setpoint | Temperature | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7
Medium Office ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Medium Office Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Medium Office Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Medium Office Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Medium Office Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Medium Office HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
Medium Office HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Medium Office HtgSetp | Thermostat Setpoint | Temperature | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6
Medium Office HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Medium Office Infil Quarter On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
Medium Office Infil Quarter On | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Medium Office Infil Quarter On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 1
Medium Office Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
MidriseApartment Apartment ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9
MidriseApartment Apartment DHW | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
MidriseApartment Apartment Equip | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
MidriseApartment Apartment HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1
MidriseApartment Apartment Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16
MidriseApartment Apartment Occ | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
MidriseApartment Apartment Operation | Operation | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment BLDG ELEVATORS | Elevator | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
MidriseApartment Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
MidriseApartment Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
MidriseApartment Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
MidriseApartment Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
MidriseApartment Corridor ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40
MidriseApartment Corridor HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
MidriseApartment Corridor Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
MidriseApartment Infil | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
MidriseApartment Office ClgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
MidriseApartment Office ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4
MidriseApartment Office ClgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
MidriseApartment Office Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
MidriseApartment Office Equip | Equipment | Dimensionless | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.33
MidriseApartment Office HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
MidriseApartment Office HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
MidriseApartment Office HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
MidriseApartment OFFICE Infil | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MidriseApartment OFFICE Infil | Infiltration | Dimensionless | WntrDsn¦SmrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 1
MidriseApartment Office Light | Lighting | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
MidriseApartment Office Light | Lighting | Dimensionless | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0.18
MidriseApartment Office Occ | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MidriseApartment Office Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment Office Operation | Operation | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MidriseApartment Office Operation | Operation | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment UnitHeater ClgSP Sch | Thermostat Setpoint | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment UnitHeater HtgSP Sch | Thermostat Setpoint | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
MidriseApartment Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Office Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132
Office Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4
Office Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Office Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Office Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3
Office Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Office Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Office Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Office Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05
Office Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office Infil Quarter On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
Office Infil Quarter On | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Office Infil Quarter On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 1
Office Misc Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05
Office Misc Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Office Misc Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
Office Misc Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office Work Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05
Office Work Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Office Work Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
Office Work Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Outpatient BLDG ELEVATORS | Elevator | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05
Outpatient BLDG ELEVATORS | Elevator | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Outpatient BLDG ELEVATORS | Elevator | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Outpatient Bldg Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
Outpatient Bldg Equip | Equipment | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Outpatient Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
Outpatient Bldg Light | Lighting | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
Outpatient Bldg Light | Lighting | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Outpatient Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
Outpatient Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
Outpatient Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
Outpatient ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
Outpatient ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Outpatient ClgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 25
Outpatient Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Outpatient Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Outpatient Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Outpatient Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Outpatient HtgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Outpatient HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Outpatient HtgSetp | Thermostat Setpoint | Temperature | Wknd | 2014-01-01 | 2014-12-31 | Constant | 18.3
Outpatient Infil | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.5
Outpatient Infil | Infiltration | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Outpatient OR ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
Outpatient OR HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3
Outpatient Radiology Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Outpatient Radiology Equip | Equipment | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0.01
Outpatient Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27
PrimarySchool BathCorrMechKitchen ClgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
PrimarySchool BathCorrMechKitchen HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
PrimarySchool Bldg Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
PrimarySchool Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
PrimarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35
PrimarySchool Bldg Equip | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
PrimarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25
PrimarySchool Bldg Equip | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
PrimarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35
PrimarySchool Bldg Light | Lighting | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
PrimarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
PrimarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PrimarySchool Cafeteria Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
PrimarySchool ClgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
PrimarySchool ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27
PrimarySchool ClgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
PrimarySchool ClgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
PrimarySchool ClgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27
PrimarySchool Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1
PrimarySchool Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6
PrimarySchool Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1
PrimarySchool Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6
PrimarySchool Gym Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
PrimarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
PrimarySchool HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
PrimarySchool HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
PrimarySchool HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
PrimarySchool HtgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
PrimarySchool HtgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16
PrimarySchool Infil | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
PrimarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1
PrimarySchool Kitchen Exhaust | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
PrimarySchool Kitchen Exhaust | Equipment | Dimensionless | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
PrimarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02
PrimarySchool Offices Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PrimarySchool Offices Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
PrimarySchool Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
PrimarySchool VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
PrimarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
PrimarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
QuickServiceRestaurant Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
QuickServiceRestaurant Bldg Equip | Equipment | Dimensionless | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.35 | 0.35 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25
QuickServiceRestaurant Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
QuickServiceRestaurant Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
QuickServiceRestaurant Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
QuickServiceRestaurant Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
QuickServiceRestaurant Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
QuickServiceRestaurant Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.3 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2
QuickServiceRestaurant Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
QuickServiceRestaurant Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
QuickServiceRestaurant Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.3 | 0.3 | 0.3 | 0.2 | 0.45 | 0.6 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.2
QuickServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
QuickServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
QuickServiceRestaurant Bldg Swh | Service Water Heating | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
QuickServiceRestaurant ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
QuickServiceRestaurant ClgSetp Kitchen | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
QuickServiceRestaurant Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
QuickServiceRestaurant Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
QuickServiceRestaurant Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
QuickServiceRestaurant Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
QuickServiceRestaurant Gas Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.09 | 0.14 | 0.1 | 0.1 | 0.22 | 0.27 | 0.24 | 0.21 | 0.14 | 0.13 | 0.15 | 0.17 | 0.17 | 0.17 | 0.15 | 0.14 | 0.12 | 0.02
QuickServiceRestaurant Gas Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
QuickServiceRestaurant Gas Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
QuickServiceRestaurant HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19
QuickServiceRestaurant HtgSetp Kitchen | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
QuickServiceRestaurant Infil Half On | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
QuickServiceRestaurant Kitchen Exhaust | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
QuickServiceRestaurant Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Retail Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Retail Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2
Retail Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Retail Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Retail Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
Retail Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
Retail Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Retail Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retail Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
Retail Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
Retail Bldg Occ | Occupancy | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Retail Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
Retail ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30
Retail ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
Retail ClgSetp | Thermostat Setpoint | Temperature | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30
Retail ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30
Retail Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Retail Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Retail Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Retail FRONT ENTRY COOLING | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 90
Retail HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
Retail HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Retail HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
Retail HtgSetp | Thermostat Setpoint | Temperature | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Retail HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
Retail INFIL FRONT | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25
Retail INFIL FRONT | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail INFIL FRONT | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Retail INFIL FRONT | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25
Retail Infil Half On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
Retail Infil Half On | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Retail Infil Half On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail Infil Half On | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1
Retail Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Schedule:Compact 1 | Unknown | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
Schedule:Compact 1 | Unknown | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
Schedule:Compact 1 | Unknown | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SecondarySchool Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SecondarySchool Auditorium Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool BLDG ELEVATORS | Elevator | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool BLDG ELEVATORS | Elevator | Dimensionless | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Bldg Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SecondarySchool Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
SecondarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.35
SecondarySchool Bldg Equip | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SecondarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25
SecondarySchool Bldg Equip | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SecondarySchool Bldg Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35
SecondarySchool Bldg Light | Lighting | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SecondarySchool Bldg Light | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SecondarySchool Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool Cafeteria Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool ClgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
SecondarySchool ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27
SecondarySchool ClgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SecondarySchool ClgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
SecondarySchool ClgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 27
SecondarySchool ClgSetp BathCorrMechKitchen | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27
SecondarySchool Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1
SecondarySchool Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6
SecondarySchool Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1
SecondarySchool Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.6
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SecondarySchool Extend Bldg Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SecondarySchool Gym Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
SecondarySchool HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SecondarySchool HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
SecondarySchool HtgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
SecondarySchool HtgSetp | Thermostat Setpoint | Temperature | Wknd¦Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
SecondarySchool HtgSetp BathCorrMechKitchen | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16
SecondarySchool Infil | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SecondarySchool Kitchen Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1
SecondarySchool Kitchen Exhaust | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SecondarySchool Kitchen Exhaust | Equipment | Dimensionless | WntrDsn¦Wknd | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SecondarySchool Kitchen Gas | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02
SecondarySchool Office Occ | Occupancy | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | Wknd | 2014-09-01 | 2014-12-31 | Constant | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool Office Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SecondarySchool Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC Operation | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SecondarySchool PSZ-AC OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool VAV Operation | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SecondarySchool VAV OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SecondarySchool Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SecondarySchool Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Small Office Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Small Office Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Small Office Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Small Office Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Small Office Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.3
Small Office Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Small Office Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Small Office Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Small Office Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Small Office Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.05
Small Office Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Small Office Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Small Office Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Small Office Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
Small Office Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Small Office ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
Small Office ClgSetp | Thermostat Setpoint | Temperature | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 26.7
Small Office ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Small Office Clothing | Clothing | Unknown | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Small Office Clothing | Clothing | Unknown | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Small Office Clothing | Clothing | Unknown | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Small Office Clothing | Clothing | Unknown | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Small Office HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
Small Office HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Small Office HtgSetp | Thermostat Setpoint | Temperature | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.6
Small Office HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Small Office Infil Quarter On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
Small Office Infil Quarter On | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
Small Office Infil Quarter On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 1
Small Office Work Eff | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallOffice PSZ-AC Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sat¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
SmallOffice PSZ-AC OA Damper | Operation | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0
SmallOffice Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SmallOffice Exterior Lights Always On | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
SmallHotel BLDG ELEVATORS | Elevator | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
SmallHotel Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
SmallHotel Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
SmallHotel Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
SmallHotel Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
SmallHotel Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
SmallHotel Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
SmallHotel Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
SmallHotel Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
SmallHotel Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
SmallHotel ClgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SmallHotel Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
SmallHotel Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
SmallHotel Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
SmallHotel Corridor Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Exercise Equip | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
SmallHotel Exercise Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
SmallHotel Exercise Occ | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
SmallHotel GuestRoom Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
SmallHotel GuestRoom Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel GuestRoom Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel GuestRoom Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
SmallHotel GuestRoom Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
SmallHotel GuestRoom Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel GuestRoom Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel GuestRoom Light | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
SmallHotel GuestRoom Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65
SmallHotel GuestRoom Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel GuestRoom Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel GuestRoom Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
SmallHotel HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SmallHotel Infil | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Infil Half On | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
SmallHotel Laundry Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SmallHotel Laundry Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Laundry Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Laundry Gas | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SmallHotel Laundry Gas | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Laundry Gas | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Laundry Light | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SmallHotel Laundry Occ | Occupancy | Dimensionless | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SmallHotel Laundry Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Laundry Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Meeting Equip | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
SmallHotel Meeting Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
SmallHotel Meeting Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Meeting Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Meeting Occ | Occupancy | Dimensionless | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0
SmallHotel Meeting Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Meeting Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Office Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
SmallHotel Office Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Office Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Office Equip | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
SmallHotel Office Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
SmallHotel Office Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Office Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Office Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SmallHotel Office Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Office Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Office Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SmallHotel StaffLounge Equip | Equipment | Dimensionless | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
SmallHotel StaffLounge Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel StaffLounge Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel StaffLounge Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05
SmallHotel StaffLounge Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel StaffLounge Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel StaffLounge Light | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05
SmallHotel StaffLounge Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
SmallHotel StaffLounge Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel StaffLounge Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel StaffLounge Occ | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
SmallHotel Storage Light | Lighting | Dimensionless | Default¦Wknd | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
SmallHotel Storage Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Storage Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel UnitHeater ClgSP Sch | Thermostat Setpoint | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40
SmallHotel UnitHeater HtgSP Sch | Thermostat Setpoint | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SmallHotel PSZ-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel PSZ-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel PTAC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel PTAC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Split-AC Operation | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Split-AC OA Damper | Operation | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
SmallHotel Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SmallHotel Exterior Lights | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
StripMall Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2
StripMall Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
StripMall Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
StripMall Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
StripMall Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
StripMall Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
StripMall Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
StripMall Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
StripMall Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
StripMall Bldg Occ | Occupancy | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
StripMall Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
StripMall ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30
StripMall ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
StripMall ClgSetp | Thermostat Setpoint | Temperature | Sun | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30
StripMall ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30
StripMall Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
StripMall Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
StripMall Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
StripMall HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
StripMall HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
StripMall HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
StripMall HtgSetp | Thermostat Setpoint | Temperature | Sun | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
StripMall HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
StripMall Infil Half On | Infiltration | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
StripMall Infil Half On | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
StripMall Infil Half On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
StripMall Infil Half On | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1
StripMall Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SuperMarket Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
SuperMarket Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2
SuperMarket Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SuperMarket Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SuperMarket Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15
SuperMarket Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
SuperMarket Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
SuperMarket Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SuperMarket Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SuperMarket Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05
SuperMarket Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
SuperMarket Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0
SuperMarket Bldg Occ | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SuperMarket Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SuperMarket Bldg Occ | Occupancy | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0
SuperMarket Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
SuperMarket Bldg Swh | Service Water Heating | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
SuperMarket Bldg Swh | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
SuperMarket Bldg Swh | Service Water Heating | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
SuperMarket ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30
SuperMarket ClgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
SuperMarket Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SuperMarket Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
SuperMarket Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
SuperMarket Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
SuperMarket HtgSetp | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
SuperMarket HtgSetp | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SuperMarket Infil Half On | Infiltration | Dimensionless | Default¦SmrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1
SuperMarket Infil Half On | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SuperMarket Infil Half On | Infiltration | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SuperMarket Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Activity | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Warehouse Bldg Equip | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse Bldg Equip | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Bldg Equip | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Bldg Equip | Equipment | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1
Warehouse Bldg Equip | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse Bldg Light | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse Bldg Light | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Bldg Light | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Bldg Light | Lighting | Dimensionless | Sun | 2014-01-01 | 2014-12-31 | Constant | 0.1
Warehouse Bldg Light | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.24 | 0.24 | 0.24 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse Bldg Occ | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.7 | 0.9 | 0.9 | 0.9 | 0.5 | 0.85 | 0.85 | 0.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse Bldg Occ | Occupancy | Dimensionless | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Bldg Occ | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Bldg Occ | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse ClgSetp | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Warehouse ClgSetp | Thermostat Setpoint | Temperature | WntrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 30
Warehouse ClgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Warehouse ClgSetp FineStorage | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
Warehouse Clothing | Clothing | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Clothing | Clothing | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Warehouse Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Warehouse Clothing | Clothing | Dimensionless | Wknd¦Wkdy | 2014-05-01 | 2014-09-30 | Constant | 0.5
Warehouse HtgSetp | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
Warehouse HtgSetp | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Warehouse HtgSetp | Thermostat Setpoint | Temperature | SmrDsn¦Sun | 2014-01-01 | 2014-12-31 | Constant | 15.5
Warehouse HtgSetp | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
Warehouse HtgSetp BulkStorage | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2
Warehouse HtgSetp FineStorage | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
Warehouse Work Eff | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise Activity Schedule | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95
ApartmentHighRise All Off | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise All On | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise Ambient Temp Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
ApartmentHighRise APT_DHW_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
ApartmentHighRise BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
ApartmentHighRise BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
ApartmentHighRise CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise CLGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise CLGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 23.9
ApartmentHighRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 29.4
ApartmentHighRise CLGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise COMPACT HVAC-ALWAYS 0 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise COMPACT HVAC-ALWAYS 1 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise COMPACT HVAC-ALWAYS 4 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
ApartmentHighRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
ApartmentHighRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
ApartmentHighRise EQP_APT_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise EQP_OFF_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
ApartmentHighRise EQP_OFF_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise Exterior_Ltg_Sch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise HTGSETP_DESIGN_OFF_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6
ApartmentHighRise HTGSETP_OFF_SCH_No_Optimum | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 15.6
ApartmentHighRise HTGSETP_OFF_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentHighRise INF_APT_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise INF_COR_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise INF_OFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise LTG_APT_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05
ApartmentHighRise LTG_COR_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise LTG_OFF_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18
ApartmentHighRise LTG_OFF_SCH | Unknown | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise LTG_OFF_SCH | Unknown | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise LTG_OFF_SCH | Unknown | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise N CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise N HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise OCC_APT_SCH | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise OCC_OFF_SCH | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise OCC_OFF_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise PLANT LOOP HIGH TEMP SCHEDULE | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
ApartmentHighRise PLANT LOOP LOW TEMP SCHEDULE | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 20
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown | Dimensionless | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 0
ApartmentHighRise PLANTCOOLINGONSCHED | Unknown | Dimensionless | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 0
ApartmentHighRise PLANTHEATINGONSCHED | Unknown | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise PLANTHEATINGONSCHED | Unknown | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise PLANTHEATINGONSCHED | Unknown | Dimensionless | Wknd¦Wkdy | 2014-10-18 | 2014-12-31 | Constant | 1
ApartmentHighRise PLANTHEATINGONSCHED | Unknown | Dimensionless | Wknd¦Wkdy | 2014-01-01 | 2014-05-08 | Constant | 1
ApartmentHighRise PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise S CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise S HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise SHW Latent fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
ApartmentHighRise SHW Sensible fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
ApartmentHighRise SHW SUPPLY TEMP SCHED | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
ApartmentHighRise SHW TARGET TEMP SCHED | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
ApartmentHighRise SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
ApartmentHighRise SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
ApartmentHighRise SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentHighRise Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise SupplyFanSch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown | ControlMode | Default | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown | ControlMode | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown | ControlMode | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 2
ApartmentHighRise ZONE CONTROL TYPE SCHED | Unknown | ControlMode | Wkdy | 2014-01-01 | 2014-12-31 | Constant | 4
ApartmentMidRise Activity Schedule | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 95
ApartmentMidRise All Off | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise All On | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise APT_DHW_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
ApartmentMidRise BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
ApartmentMidRise BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
ApartmentMidRise CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4
ApartmentMidRise CLGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.9
ApartmentMidRise CLGSETP_OFF_SCH_No_Setback | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.4
ApartmentMidRise CLGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise COMPACT HVAC-ALWAYS 0 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise COMPACT HVAC-ALWAYS 18.3333338190008 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3333
ApartmentMidRise COMPACT HVAC-ALWAYS 4 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
ApartmentMidRise Constant Mains Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12
ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
ApartmentMidRise ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
ApartmentMidRise EQP_APT_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise EQP_OFF_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
ApartmentMidRise EQP_OFF_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise Exterior_Ltg_Sch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise Hot Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
ApartmentMidRise HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise HTGSETP_OFF_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise HTGSETP_OFF_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentMidRise INF_APT_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise INF_COR_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise INF_OFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise LTG_APT_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.13 | 0.14 | 0.13 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.14 | 0.2 | 0.27 | 0.32 | 0.32 | 0.22 | 0.12 | 0.05
ApartmentMidRise LTG_COR_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise LTG_OFF_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18
ApartmentMidRise LTG_OFF_SCH | Unknown | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise LTG_OFF_SCH | Unknown | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
ApartmentMidRise LTG_OFF_SCH | Unknown | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise N CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise N HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise OCC_APT_SCH | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise OCC_OFF_SCH | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise OCC_OFF_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise S CLGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise S HTGSETP_APT_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentMidRise Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
Hospital AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_ELEVATORS | Elevator | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital BLDG_ELEVATORS | Elevator | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital BLDG_EQUIP_EXTD_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_EQUIP_EXTD_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_EQUIP_EXTD_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_EQUIP_EXTD_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_EQUIP_EXTD_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXTD_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXTD_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_EXTD_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_EXTD_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_EXTD_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_LOBBYFLR5_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_NURSEFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_NURSEFLR234_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_RADIOLOGY_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital BLDG_OA_FRAC_SCH | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_OA_FRAC_SCH | OA Air | Dimensionless | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
Hospital BLDG_OCC_EXTD_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_OCC_EXTD_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_OCC_EXTD_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_OCC_EXTD_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_OCC_EXTD_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
Hospital BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating | Dimensionless | Default¦WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital BLDG_SWH_EXTD_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3
Hospital BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0
Hospital CLGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
Hospital CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Hospital CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
Hospital CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
Hospital Cool-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
Hospital CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
Hospital Dishwashing Booster Setpoint Temp Schedule | Service Water Heating | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
Hospital Dishwashing Booster Water Inlet Temp Schedule | Service Water Heating | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
Hospital ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital ER_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital ER_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital ER_Trauma1_Flr_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital ER_Trauma1_Flr_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ER_Trauma1_Flr_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital ER_Trauma2_Flr_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital ER_Trauma2_Flr_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ER_Trauma2_Flr_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Heat-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
Hospital Hours_of_operation | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital HTGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
Hospital Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
Hospital HVACOperationSchd | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82
Hospital ICU_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital ICU_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital INFIL_SCH_PNNL | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25
Hospital Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458 | 0.4458
Hospital Kitchen_Exhaust_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital Kitchen_Flr_5 sub cat Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital Kitchen_Flr_5 sub cat Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital Kitchen_Flr_5 sub cat Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Kitchen_Flr_5 sub catHot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital Kitchen_SAT_SCH | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
Hospital Labs_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Labs_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Lab_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital Lab_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital Lab_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Lab_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital Lab_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital Lab_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital Lab_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Lab_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital Laundry Setpoint Temp Schedule | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
Hospital LAUNDRY_SWH_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital MaxRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital MinRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40
Hospital MinRelHumSetSch_addDI | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
Hospital MinRelHumSetSch_addDI_ICU | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 35
Hospital OR1_Flr_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital OR1_Flr_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital OR1_Flr_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital OR1_Flr_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital OR2_Mult5_Flr_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital OR2_Mult5_Flr_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital OR2_Mult5_Flr_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital OR3_Flr_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital OR3_Flr_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital OR3_Flr_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital OR3_Flr_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital OR4_Flr_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital OR4_Flr_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital OR4_Flr_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital OR4_Flr_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital OR_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital OR_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital OR_MinSA_Sched | Unknown | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital OR_MinSA_Sched | Unknown | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital OR_MinSA_Sched | Unknown | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital OR_MinSA_Sched | Unknown | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital Patrms_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Patrms_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom2_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom2_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom2_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom2_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom2_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom2_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom2_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom2_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom4_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom4_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom4_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom4_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom4_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom4_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom4_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom4_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom6_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom6_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom6_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom6_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom6_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom6_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom6_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom6_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom8_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom8_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom8_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom8_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PatRoom8_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PatRoom8_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PatRoom8_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PatRoom8_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PhysTherapy_Flr_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital PhysTherapy_Flr_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital PhysTherapy_Flr_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital Radiology_Flr_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
Hospital Radiology_Flr_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
Hospital Radiology_Flr_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Radiology_Flr_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
Hospital ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital scheduleOSCBasementFloorTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital scheduleOSCBasementLowerWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital scheduleOSCBasementUpperWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital scheduleOSCBasementWallSurfaceTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
Hospital SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Hospital Tower-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1
Hospital VAV_ER_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
Hospital VAV_ICU_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
Hospital VAV_LABS_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital VAV_OR_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
Hospital VAV_PATRMS_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
Hospital VAV_SAT_SCH | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
Hospital walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.052 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Hospital walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Hospital walkin_occ_lght_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.104 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.208 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.26 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.1
Hospital WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BASEMENT_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge BASEMENT_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BASEMENT_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BASEMENT_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge BASEMENT_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
HotelLarge BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
HotelLarge BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_OFFICE_BSMT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
HotelLarge BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
HotelLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
HotelLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
HotelLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
HotelLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
HotelLarge Booster Water Inlet Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Booster Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
HotelLarge CLGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
HotelLarge CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelLarge CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
HotelLarge CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
HotelLarge Cool-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
HotelLarge CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
HotelLarge Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelLarge EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelLarge EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelLarge EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
HotelLarge ExerciseRoom_Eqp_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelLarge ExerciseRoom_Occ_Sch | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelLarge Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Exterior_Ltg_Sch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
HotelLarge FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge FLR_3_DOAS_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.17
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge GuestRoom_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5
HotelLarge GuestRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge GuestRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge GuestRoom_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65
HotelLarge GuestRoom_SWH_Sch | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge GuestRoom_SWH_Sch | Service Water Heating | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelLarge Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
HotelLarge Hours_of_operation | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge HTGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
HotelLarge Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
HotelLarge HVACOperationSchd | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelLarge INFIL_QUARTER_ON_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
HotelLarge INFIL_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872 | 0.50872
HotelLarge Kitchen_Elec_Equip_SCH | Equipment | Dimensionless | Default¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge Kitchen_Elec_Equip_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Kitchen_Elec_Equip_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3
HotelLarge Kitchen_Exhaust_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Kitchen_Flr_6 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Kitchen_Flr_6 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Kitchen_Flr_6 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Kitchen_Gas_Equip_SCH | Equipment | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge Kitchen_Gas_Equip_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Kitchen_Gas_Equip_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.25
HotelLarge Laundry Setpoint Temp Schedule | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge LaundryRoom_Occ_Sch | Occupancy | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge LaundryRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge LaundryRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge LaundryRoom_SWH_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge LAUNDRY_SWH_SCH | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge Lobby_Eqp_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelLarge Lobby_Eqp_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Lobby_Eqp_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Lobby_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelLarge Lobby_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Lobby_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Lobby_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelLarge MaxRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge MeetingRoom_Eqp_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelLarge MeetingRoom_Occ_Sch | Occupancy | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelLarge MeetingRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge MeetingRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge MinRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelLarge Off During Unoccupied Period | Occupancy | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge Office_Eqp_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelLarge Office_Eqp_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Office_Eqp_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Office_Eqp_Sch | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
HotelLarge Office_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge Office_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Office_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Office_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_1_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_1_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_1_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_1_Flr_6 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_1_Flr_6 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_1_Flr_6 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_2_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_2_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_2_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_2_Flr_6 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_2_Flr_6 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_2_Flr_6 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_5_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_5_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_5_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
HotelLarge Room_6_Flr_3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelLarge Room_6_Flr_3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelLarge Room_6_Flr_3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelLarge scheduleOSCBasementFloorTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge scheduleOSCBasementLowerWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge scheduleOSCBasementUpperWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge scheduleOSCBasementWallSurfaceTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
HotelLarge Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
HotelLarge SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelLarge Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
HotelLarge SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge SWHSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelLarge walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.156 | 0.208 | 0.208 | 0.156 | 0.156 | 0.156 | 0.156 | 0.104 | 0.104 | 0.104 | 0.104 | 0.104 | 0.26 | 0.364 | 0.416 | 0.312 | 0.26 | 0.156
HotelLarge walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelLarge walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelLarge walkin_occ_lght_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.104 | 0.052 | 0.052 | 0.052 | 0.052 | 0.156 | 0.156 | 0.208 | 0.208 | 0.156 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.364 | 0.364 | 0.364 | 0.312 | 0.156
HotelLarge walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.104 | 0.078 | 0.052 | 0.052 | 0.052 | 0.104 | 0.208 | 0.26 | 0.208 | 0.208 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.312 | 0.416 | 0.468 | 0.416 | 0.312 | 0.156
HotelLarge WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall Activity_Sch | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 132
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 23.888 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall Adva5F_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 18.334 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall Adva5F_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall Adva_EmployeeLounge_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667
HotelSmall Adva_EmployeeLounge_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333
HotelSmall Adva_ExerciseCenter_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667
HotelSmall Adva_ExerciseCenter_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333
HotelSmall Adva_MeetingRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 26.667 | 26.667 | 26.667 | 26.667 | 26.667
HotelSmall Adva_MeetingRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.333 | 18.333 | 18.333 | 18.333 | 18.333
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall AlwaysOff | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall AlwaysOff_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall AlwaysOn | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall AlwaysOn_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall Base_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall Base_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
HotelSmall BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelSmall BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelSmall BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_EMPLOYEELOUNGE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_EXERCENTER_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_FRONTLOUNGE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_GUESTROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelSmall BLDG_LIGHT_LAUNDRY_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_MECHROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_MEETINGROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_RESTROOM_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_STAIR_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall CommonArea_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.889
HotelSmall CommonArea_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall CommonArea_Infil_Sch | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25
HotelSmall CommonArea_Infil_Sch | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall CommonArea_Infil_Sch | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall COMPACT HVAC-ALWAYS 0 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall COMPACT HVAC-ALWAYS 1 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall COMPACT HVAC-ALWAYS 4 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
HotelSmall ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelSmall ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
HotelSmall EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall EmployeeLounge_Eqp_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall EmployeeLounge_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
HotelSmall ExerciseCenter_Eqp_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall ExerciseCenter_Occ_Sch | Occupancy | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall Exterior_Ltg_Sch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.3 | 0.62 | 0.9 | 0.62 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.21 | 0.4 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall GuestRoom_Eqp_Sch_Adva | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.62 | 0.9 | 0.43 | 0.43 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.19 | 0.48 | 0.48 | 0.46 | 0.62 | 0.69 | 0.34 | 0.09
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall GuestRoom_Eqp_Sch_Base | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall GuestRoom_Infil_Sch | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.25
HotelSmall GuestRoom_Infil_Sch | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall GuestRoom_Infil_Sch | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall GuestRoom_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall GuestRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall GuestRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall GuestRoom_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelSmall GuestRoom_SHW_Sch | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall GuestRoom_SHW_Sch | Service Water Heating | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelSmall Heat Exchanger Supply Air Temp Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 14
HotelSmall INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall LaundryRoom_Eqp_Elec_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall LaundryRoom_Eqp_Gas_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall LaundryRoom_Occ_Sch | Occupancy | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall LaundryRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall LaundryRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall LaundryRoom_SHW_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall Lobby_Eqp_Sch | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall Lobby_Eqp_Sch | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall Lobby_Eqp_Sch | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall Lobby_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall Lobby_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall Lobby_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall Lobby_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall MeetingRoom_Eqp_Sch | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall MeetingRoom_Occ_Sch | Occupancy | Dimensionless | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall MeetingRoom_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall MeetingRoom_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall N Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall N Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall Off During Unoccupied Period | Occupancy | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall Office_Occ_Sch | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall Office_Occ_Sch | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall Office_Occ_Sch | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall Office_Occ_Sch | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall OFF_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall OFF_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall OFF_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall OFF_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall S Adva_OccGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall S Adva_OccGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.111
HotelSmall SemiHeated_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 7.2
HotelSmall SHW Latent fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
HotelSmall SHW Laundry Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
HotelSmall SHW Sensible fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
HotelSmall SHW Shower Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelSmall SHWSys Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1
HotelSmall SHWSysLaundry Water Heater Setpoint Temperature Schedule | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelSmall SHWSysLaundry-Loop-Temp-Schedule | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelSmall SHWSysShower Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelSmall SHWSysShower-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelSmall Sliding_Doors_Ventilation_Availability_SCH | Unknown | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
HotelSmall VacGuestRoom_ClgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.333
HotelSmall VacGuestRoom_HtgSP_Sch | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.889
OfficeLarge ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
OfficeLarge AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeLarge ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
OfficeLarge BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3
OfficeLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
OfficeLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
OfficeLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
OfficeLarge BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge CLGSETP_DC_SCH | Thermostat Setpoint | Temperature | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 27
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24
OfficeLarge CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeLarge CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
OfficeLarge CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
OfficeLarge Cool-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
OfficeLarge CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge Core_bottom sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge Core_bottom sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeLarge Core_bottom sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeLarge Core_bottom sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeLarge Core_mid sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge Core_mid sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeLarge Core_mid sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeLarge Core_mid sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeLarge Core_top sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge Core_top sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeLarge Core_top sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeLarge Core_top sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeLarge CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
OfficeLarge DataCenter_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge DataCenter_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge DC_MinRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
OfficeLarge Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
OfficeLarge ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeLarge Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
OfficeLarge EXTERIOR_LIGHT_SCH | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
OfficeLarge FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge Heat-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
OfficeLarge Hours_of_operation | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge Hours_of_operation | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge Hours_of_operation | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge HTGSETP_DC_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_CAV_bas | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge HVACOperationSchd | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge HVACOperationSchd | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge HVACOperationSchd | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82
OfficeLarge INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge INFIL_HALF_ON_SCH | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge INFIL_HALF_ON_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1
OfficeLarge INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge INFIL_SCH | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge INFIL_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
OfficeLarge INFIL_SCH_PNNL | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge INFIL_SCH_PNNL | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge INFIL_SCH_PNNL | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge PLANT LOOP HIGH TEMP SCHEDULE | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.33
OfficeLarge PLANT LOOP LOW TEMP SCHEDULE | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 5
OfficeLarge PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge scheduleOSCBasementFloorTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge scheduleOSCBasementLowerWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge scheduleOSCBasementUpperWallTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge scheduleOSCBasementWallSurfaceTemp | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeLarge SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
OfficeLarge SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeLarge SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeLarge SupplyFanSch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeLarge Tower-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.1
OfficeLarge WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
OfficeMedium AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium BLDG_ELEVATORS | Elevator | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69
OfficeMedium BLDG_ELEVATORS | Elevator | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium BLDG_ELEVATORS | Elevator | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0
OfficeMedium BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814
OfficeMedium BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium BLDG_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.38414 | 0.38414 | 0.48018 | 0.48018 | 0.48018 | 0.48018 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.33613 | 0.28811 | 0.28811 | 0.23814 | 0.23814 | 0.23814 | 0.23814 | 0.23814
OfficeMedium BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.31751 | 0.38414 | 0.38414 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.76829 | 0.86432 | 0.86432 | 0.86432 | 0.86432 | 0.48018 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414 | 0.38414
OfficeMedium BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium BLDG_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0904 | 0.0904 | 0.2712 | 0.2712 | 0.2712 | 0.2712 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.1356 | 0.0452 | 0.0452 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.0904 | 0.2712 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.8136 | 0.452 | 0.2712 | 0.2712 | 0.1808 | 0.1808 | 0.0904 | 0.0452
OfficeMedium BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05
OfficeMedium BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
OfficeMedium BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦WntrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24
OfficeMedium CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeMedium CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
OfficeMedium CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
OfficeMedium Cool-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
OfficeMedium CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium Core_bottom sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Core_bottom sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Core_bottom sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Core_bottom sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Core_mid sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Core_mid sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Core_mid sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Core_mid sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Core_top sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Core_top sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Core_top sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Core_top sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
OfficeMedium Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.69
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0
OfficeMedium Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeMedium Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
OfficeMedium FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium Heat-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
OfficeMedium Hours_of_operation | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium Hours_of_operation | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium Hours_of_operation | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_bot | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_mid | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_PACU_VAV_top | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.6 | 19.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
OfficeMedium HVACOperationSchd | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium HVACOperationSchd | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium HVACOperationSchd | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OfficeMedium INFIL_SCH_PNNL | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium INFIL_SCH_PNNL | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium INFIL_SCH_PNNL | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium Perimeter_bot_ZN_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_bot_ZN_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_bot_ZN_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_bot_ZN_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_bot_ZN_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_bot_ZN_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_bot_ZN_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_bot_ZN_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_bot_ZN_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_bot_ZN_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_bot_ZN_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_bot_ZN_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_mid_ZN_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_mid_ZN_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_mid_ZN_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_mid_ZN_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_mid_ZN_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_mid_ZN_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_mid_ZN_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_mid_ZN_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_mid_ZN_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_mid_ZN_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_mid_ZN_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_mid_ZN_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_top_ZN_1 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_top_ZN_1 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_top_ZN_1 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_top_ZN_2 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_top_ZN_2 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_top_ZN_2 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_top_ZN_3 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_top_ZN_3 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_top_ZN_3 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium Perimeter_top_ZN_4 sub cat Latent fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeMedium Perimeter_top_ZN_4 sub cat Sensible fract sched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeMedium Perimeter_top_ZN_4 sub cat Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeMedium PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeMedium SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
OfficeMedium SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeMedium WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
OfficeSmall AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeSmall ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall BLDG_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall BLDG_LIGHT_SCH | Lighting | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18
OfficeSmall BLDG_OCC_SCH | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89
OfficeSmall CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
OfficeSmall CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 23.89
OfficeSmall CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeSmall CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
OfficeSmall CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
OfficeSmall CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall Core_ZN Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OfficeSmall Core_ZN Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OfficeSmall Core_ZN Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OfficeSmall Core_ZN Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 48.8
OfficeSmall CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
OfficeSmall Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
OfficeSmall Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OfficeSmall Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
OfficeSmall HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21.11
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
OfficeSmall HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
OfficeSmall HVACOperationSchd | Operation | Availability | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall HVACOperationSchd | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OfficeSmall HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeSmall INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall INFIL_QUARTER_ON_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OfficeSmall MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
OfficeSmall Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
OfficeSmall SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OfficeSmall SHWSys1 Water Heater Ambient Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
OfficeSmall SHWSys1 Water Heater Setpoint Temperature Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeSmall SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OfficeSmall WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
OutPatientHealthCare AHU-1_ExtraElecHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare AHU-1_ExtraWaterHeatC_Sch | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare AHU-1_OAminOAFracSchedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.33
OutPatientHealthCare AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare BLDG_CAV_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_CAV_SCH_HUMID | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OutPatientHealthCare BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare BLDG_ELEVATORS | Elevator | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_ELEVATORS | Elevator | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_EQUIP_SCH_BASE | Equipment | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_EXAM_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare BLDG_LIGHT_TOILET_SCH | Lighting | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare BLDG_OA_FRAC_SCH | OA Air | Dimensionless | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare BLDG_OA_SCH | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare BLDG_OA_SCH | OA Air | Dimensionless | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
OutPatientHealthCare BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
OutPatientHealthCare CAV_SAT_SCH | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 25
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 22.2
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
OutPatientHealthCare CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
OutPatientHealthCare CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
OutPatientHealthCare Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05
OutPatientHealthCare Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OutPatientHealthCare Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Anesthesia Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 MRI Control Room Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 MRI Room Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 MRI Room Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 MRI Room Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Operating Room 1 humidity sched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Operating Room 1 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Operating Room 2 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Operating Room 3 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 PACU Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 PACU Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 PACU Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 PACU Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Procedure Room Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Recovery Room Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 1 Step Down Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 1 Step Down Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 1 Step Down Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 2 X-Ray Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 2 X-Ray Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 2 X-Ray Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
OutPatientHealthCare HeatSys1 Loop Setpoint Sched | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.2
OutPatientHealthCare Hours_of_operation | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Constant | 18.3
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
OutPatientHealthCare HVACOperationSchd | Operation | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.5
OutPatientHealthCare INFIL_HALF_ON_SCH | Infiltration | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare INFIL_SCH | Infiltration | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 0.25
OutPatientHealthCare INFIL_SCH | Infiltration | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare MaxRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare MinRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 40
OutPatientHealthCare MinRelHumSetSch_addDI | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
OutPatientHealthCare OR_CLGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare OR_HTGSETP_SCH | Thermostat Setpoint | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 18.3
OutPatientHealthCare OR_MinSA_Sched | Unknown | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
OutPatientHealthCare OR_MinSA_Sched | Unknown | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare OR_MinSA_Sched | Unknown | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OutPatientHealthCare Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 11.1
OutPatientHealthCare SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
OutPatientHealthCare SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
OutPatientHealthCare SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare SWHSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
OutPatientHealthCare VAV_SAT_SCH | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
OutPatientHealthCare WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
RestaurantFastFood AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RestaurantFastFood ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood BLDG_EQUIP_SCH | Equipment | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood BLDG_LIGHT_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantFastFood BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantFastFood BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
RestaurantFastFood BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.11
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 28.33 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantFastFood CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
RestaurantFastFood CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
RestaurantFastFood CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
RestaurantFastFood DOOR_INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258
RestaurantFastFood DOOR_INFIL_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood DOOR_INFIL_SCH | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood DOOR_INFIL_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363
RestaurantFastFood DOOR_INFIL_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258
RestaurantFastFood Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
RestaurantFastFood Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood FF_GAS_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29
RestaurantFastFood Hours_of_operation | Operation | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.22 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RestaurantFastFood HVACOperationSchd | Operation | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood INFIL_SCH_PNNL | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.53051 | 0 | 0 | 0 | 0 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051 | 0.53051
RestaurantFastFood Kitchen Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
RestaurantFastFood Kitchen Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
RestaurantFastFood Kitchen Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RestaurantFastFood Kitchen Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood Kitchen_Exhaust_SCH | Equipment | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood MinOA_FFKitch_Sched | OA Air | Availability | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood MinOA_FFKitch_Sched | OA Air | Availability | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
RestaurantFastFood SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantFastFood SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345
RestaurantFastFood VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241
RestaurantFastFood walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156
RestaurantFastFood walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantFastFood walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantFastFood walkin_occ_lght_SCH | Occupancy | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156
RestaurantFastFood WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
RestaurantSitDown AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RestaurantSitDown ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown BLDG_EQUIP_SCH | Equipment | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown BLDG_LIGHT_DINING_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown BLDG_LIGHT_SCH | Lighting | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantSitDown BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantSitDown BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
RestaurantSitDown BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
RestaurantSitDown Booster Water Inlet Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantSitDown Booster Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_KITCHEN_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 26 | 30 | 30 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 30 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
RestaurantSitDown CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
RestaurantSitDown CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
RestaurantSitDown CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown DOOR_INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258
RestaurantSitDown DOOR_INFIL_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown DOOR_INFIL_SCH | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown DOOR_INFIL_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363
RestaurantSitDown DOOR_INFIL_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258
RestaurantSitDown Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
RestaurantSitDown Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
RestaurantSitDown Hours_of_operation | Operation | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19
RestaurantSitDown HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 19
RestaurantSitDown HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
RestaurantSitDown HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
RestaurantSitDown Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
RestaurantSitDown HVACOperationSchd | Operation | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantSitDown INFIL_SCH_PNNL | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.93371 | 0 | 0 | 0 | 0 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371 | 0.93371
RestaurantSitDown Kitchen Water Equipment Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
RestaurantSitDown Kitchen Water Equipment Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
RestaurantSitDown Kitchen Water Equipment Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RestaurantSitDown Kitchen Water Equipment Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown Kitchen_Exhaust_SCH | Equipment | Availability | Default¦WntrDsn¦SmrDsn¦Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown MaxRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantSitDown MinOA_FFKitch_Sched | OA Air | Availability | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65
RestaurantSitDown MinOA_FFKitch_Sched | OA Air | Availability | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.65
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown MinOA_SDKitch_Sched | OA Air | Availability | Default¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown MinOA_SDKitch_Sched | OA Air | Availability | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown MinRelHumSetSch | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 30
RestaurantSitDown PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment | Dimensionless | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown Rest_GAS_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.29
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
RestaurantSitDown Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
RestaurantSitDown SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown SWHSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
RestaurantSitDown SWHSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantSitDown SWHSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345
RestaurantSitDown VESTIBULE_DOOR_INFIL_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241
RestaurantSitDown walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.312 | 0.312 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.416 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.26 | 0.156
RestaurantSitDown walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RestaurantSitDown walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RestaurantSitDown walkin_occ_lght_SCH | Occupancy | Dimensionless | Sun¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.156 | 0.156 | 0.26 | 0.26 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.364 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.26 | 0.156
RestaurantSitDown WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
RetailStandalone AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RetailStandalone ALWAYS_OFF | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_ELEVATORS | Elevator | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0
RetailStandalone BLDG_ELEVATORS | Elevator | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0
RetailStandalone BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0
RetailStandalone BLDG_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
RetailStandalone BLDG_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
RetailStandalone BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_BACK_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_ENTRY_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_FRONT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
RetailStandalone BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone BLDG_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
RetailStandalone BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
RetailStandalone BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
RetailStandalone BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
RetailStandalone BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStandalone CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
RetailStandalone CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
RetailStandalone CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
RetailStandalone CoolingCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
RetailStandalone Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
RetailStandalone Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStandalone Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone FAN_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone FrontEntry_CoilSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone FrontEntry_FanSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone FRONT_ENTRY_COOLING | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 100
RetailStandalone Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
RetailStandalone Hot Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RetailStandalone Hours_of_operation | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone Hours_of_operation | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone Hours_of_operation | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | Temperature | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStandalone HTGSETP_SCH_FrontEntry_STD2013 | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_PSZ_AC_2 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 50
RetailStandalone HVACOperationSchd | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone HVACOperationSchd | Operation | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone HVACOperationSchd | Operation | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RetailStandalone INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStandalone INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone INFIL_HALF_ON_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone INFIL_HALF_ON_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
RetailStandalone INFIL_HALF_ON_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1
RetailStandalone INFIL_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone INFIL_SCH | Infiltration | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone INFIL_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
RetailStandalone INFIL_SCH | Infiltration | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
RetailStandalone INFIL_SCH_PNNL | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStandalone INFIL_SCH_PNNL | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
RetailStandalone INFIL_SCH_PNNL | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone PlantOnSched | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone ReheatCoilAvailSched | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
RetailStandalone Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
RetailStandalone SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStandalone WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
RetailStripmall AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
RetailStripmall ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
RetailStripmall CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1
RetailStripmall CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1
RetailStripmall Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
RetailStripmall Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Hot Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
RetailStripmall INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStripmall MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Fri¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Constant | 23.89
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall Type1_EQUIP_SCH | Equipment | Dimensionless | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall Type1_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type1_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type1_EQUIP_SCH | Equipment | Dimensionless | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
RetailStripmall Type1_FAN_SCH | Unknown | Availability | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type1_FAN_SCH | Unknown | Availability | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall Type1_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type1_Infil_SCH | Infiltration | Dimensionless | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall Type1_Infil_SCH | Infiltration | Dimensionless | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall Type1_LIGHT_SCH | Lighting | Dimensionless | Default¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5
RetailStripmall Type1_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type1_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type1_LIGHT_SCH | Lighting | Dimensionless | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | Default¦SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type1_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type1_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05
RetailStripmall Type1_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type1_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type1_OCC_SCH | Occupancy | Dimensionless | Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2
RetailStripmall Type1_OCC_SCH | Occupancy | Dimensionless | Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05
RetailStripmall Type1_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1
RetailStripmall Type1_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat¦Fri | 2014-01-01 | 2014-12-31 | Hourly | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall Type1_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Mon¦Tue¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type2_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type2_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type2_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type2_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_FAN_SCH | Unknown | Availability | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_FAN_SCH | Unknown | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_FAN_SCH | Unknown | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type2_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type2_Infil_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type2_Infil_SCH | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type2_Infil_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall Type2_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type2_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type2_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall Type2_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type2_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type2_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0
RetailStripmall Type2_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type2_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 23.89
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type3_CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall Type3_EQUIP_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_EQUIP_SCH | Equipment | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type3_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type3_EQUIP_SCH | Equipment | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_FAN_SCH | Unknown | Availability | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_FAN_SCH | Unknown | Availability | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_FAN_SCH | Unknown | Availability | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
RetailStripmall Type3_HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Sat | 2014-01-01 | 2014-12-31 | Hourly | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall Type3_Infil_SCH | Infiltration | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type3_Infil_SCH | Infiltration | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall Type3_Infil_SCH | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall Type3_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type3_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type3_LIGHT_SCH | Lighting | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_MinOA_MotorizedDamper_SCH | OA Air | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall Type3_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_OCC_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
RetailStripmall Type3_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
RetailStripmall Type3_OCC_SCH | Occupancy | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0
RetailStripmall Type3_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn¦Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0
RetailStripmall Type3_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
SchoolPrimary AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolPrimary ALWAYS_OFF | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary ALWAYS_ON | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolPrimary Bath_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35
SchoolPrimary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0
SchoolPrimary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sat | 2014-09-16 | 2014-12-31 | Constant | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0
SchoolPrimary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary Booster Water Inlet Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolPrimary Booster Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | Temperature | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_Setup | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolPrimary CLGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6
SchoolPrimary CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1
SchoolPrimary CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1
SchoolPrimary CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1
SchoolPrimary CoolingCoilAvailSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
SchoolPrimary Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
SchoolPrimary Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
SchoolPrimary Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary FAN_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
SchoolPrimary Hours_of_operation | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary Hours_of_operation | Operation | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | Temperature | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_Setback | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_VAV_OTHER | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_VAV_POD_1 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_VAV_POD_2 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_VAV_POD_3 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolPrimary HTGSETP_SCH_YES_OPTIMUM_original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65
SchoolPrimary HVACOperationSchd | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary HVACOperationSchd | Operation | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary INFIL_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
SchoolPrimary INFIL_SCH_PNNL | Infiltration | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary INFIL_SCH_PNNL | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0.81667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1
SchoolPrimary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolPrimary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02
SchoolPrimary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolPrimary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary MinOA_Kitchen_Sched | Equipment | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary MinOA_Kitchen_Sched | Equipment | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary MinOA_MotorizedDamper_Sched | OA Air | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary PlantOnSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary ReheatCoilAvailSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
SchoolPrimary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
SchoolPrimary SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
SchoolPrimary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolPrimary SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolPrimary VAV-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolPrimary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary ACTIVITY_SCH | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 120
SchoolSecondary AIR_VELO_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolSecondary ALWAYS_OFF | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary ALWAYS_ON | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolSecondary Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Service Water Heating | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolSecondary Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary BLDG_ELEVATORS | Elevator | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_ELEVATORS | Elevator | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3
SchoolSecondary BLDG_ELEVATORS | Elevator | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.35
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.25
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.35
SchoolSecondary BLDG_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_BATH_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CLASSROOM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_CORRIDOR_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_GYM_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LIBRARY_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_LOBBYFLR1_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary BLDG_LIGHT_SCH | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Wknd | 2014-06-16 | 2014-09-15 | Constant | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-15 | Constant | 0
SchoolSecondary BLDG_OCC_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Auditorium | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Cafeteria | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Extend | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Gym | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary BLDG_OCC_SCH_Offices | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sat | 2014-09-16 | 2014-12-31 | Constant | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-09-16 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sun¦Sat | 2014-06-16 | 2014-09-15 | Constant | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-06-16 | 2014-09-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Sun¦Sat | 2014-01-01 | 2014-06-15 | Constant | 0
SchoolSecondary BLDG_SWH_SCH | Service Water Heating | Dimensionless | Wkdy | 2014-01-01 | 2014-06-15 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary Booster Water Inlet Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary Booster Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82.22
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_NO_SETBACK | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_Setup | Thermostat Setpoint | Temperature | Default¦WntrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_Setup | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 29.44
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 24
SchoolSecondary CLGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary CLOTHING_SCH | Clothing | ActivityLevel | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.6
SchoolSecondary CLOTHING_SCH | Clothing | ActivityLevel | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1.1
SchoolSecondary CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 1.1
SchoolSecondary CLOTHING_SCH | Clothing | ActivityLevel | Wknd¦Wkdy | 2014-01-01 | 2014-04-30 | Constant | 1.1
SchoolSecondary CoolingCoilAvailSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary CW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 6.7
SchoolSecondary Dual Zone Control Type Sched | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.3
SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | Lighting | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
SchoolSecondary Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
SchoolSecondary FAN_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary Heating-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 16
SchoolSecondary Hours_of_operation | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary Hours_of_operation | Operation | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_NO_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_PSZ_AC_1_5 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_PSZ_AC_2_6 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_PSZ_AC_3_7 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_PSZ_AC_4_8 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_PSZ_AC_5_9 | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | Temperature | Default¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_Setback | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_YES_OPTIMUM | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.6
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 21
SchoolSecondary HTGSETP_SCH_Yes_Optimum_Original | Thermostat Setpoint | Temperature | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary Humidity Setpoint Schedule | Unknown | Unknown | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 65
SchoolSecondary HVACOperationSchd | Operation | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary HVACOperationSchd | Operation | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary HW-Loop-Temp-Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 82
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0
SchoolSecondary INFIL_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary INFIL_SCH_PNNL | Infiltration | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary INFIL_SCH_PNNL | Infiltration | Dimensionless | SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0.7463 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1
SchoolSecondary KITCHEN_ELEC_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0
SchoolSecondary Kitchen_Exhaust_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary Kitchen_Exhaust_SCH_DCV | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Default¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.02
SchoolSecondary KITCHEN_GAS_EQUIP_SCH | Equipment | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 55
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.05
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Equipment | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.2
SchoolSecondary Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Equipment | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | Default | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Equipment | ActivityLevel | WntrDsn¦SmrDsn¦Wknd¦Mon¦Wed¦Thu | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Equipment | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air | Availability | Default | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary MinOA_MotorizedDamper_Sched | OA Air | Availability | WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary MinOA_Sched | OA Air | Availability | Default¦WntrDsn¦SmrDsn¦Wkdy | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary PlantOnSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary ReheatCoilAvailSched | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 13
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-10-01 | 2014-12-31 | Constant | 13
SchoolSecondary Seasonal-Reset-Supply-Air-Temp-Sch | Unknown | Temperature | Wknd¦Wkdy | 2014-01-01 | 2014-03-31 | Constant | 13
SchoolSecondary SHADING_SCH | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary SHWSys1 Water Heater Ambient Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 22
SchoolSecondary SHWSys1 Water Heater Setpoint Temperature Schedule Name | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary SHWSys1-Loop-Temp-Schedule | Service Water Heating | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
SchoolSecondary VAV-Supply-Air-Temp-Sch | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 12.8
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1773
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-09-01 | 2014-12-31 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wknd | 2014-07-01 | 2014-09-01 | Constant | 0.1773
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-07-01 | 2014-09-01 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wknd | 2014-01-01 | 2014-06-30 | Constant | 0.1773
SchoolSecondary walkin_occ_lght_SCH | Occupancy | Dimensionless | Wkdy | 2014-01-01 | 2014-06-30 | Hourly | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.468 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary WORK_EFF_SCH | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Always Off Schedule | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Always On Schedule | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse ALWAYS_OFF | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse ALWAYS_ON | Unknown | Availability | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.18
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse BLDG_LIGHT_OFFICE_SCH | Lighting | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.1
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse BLDG_LIGHT_STORAGE_SCH | Lighting | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse BLDG_OCC_SCH | Occupancy | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse BLDG_OCC_SCH | Occupancy | Dimensionless | WntrDsn¦SmrDsn¦Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse Bulk Storage Heating Setpoint Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 10
Warehouse COMPACT HVAC-ALWAYS 1 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse COMPACT HVAC-ALWAYS 4 | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 4
Warehouse Exterior_Lgt_189_1 | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0.5
Warehouse Exterior_Lgt_ALWAYS_ON | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Exterior_lighting_schedule_a | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Exterior_lighting_schedule_b | Lighting | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Exterior_Ltg_Sch | Unknown | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
Warehouse FanSched | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse FanSched | Unknown | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse FanSched | Unknown | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse Fine Storage Cooling Setpoint Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 26.7
Warehouse Fine Storage Heating Setpoint Schedule | Unknown | Temperature | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 15.56
Warehouse Hot Water Setpoint Temp Schedule | Unknown | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 60
Warehouse INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse INFIL_Door_Opening_SCH | Infiltration | Dimensionless | Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
Warehouse MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse MinOA_MotorizedDamper_Sched | OA Air | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse MinOA_Sched | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse OA Damper Always ON Schedule | OA Air | Dimensionless | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse OA Damper Off during off hrs Schedule | OA Air | Dimensionless | Default¦Sun | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse OA Damper Off during off hrs Schedule | OA Air | Dimensionless | WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse OA Damper Off during off hrs Schedule | OA Air | Dimensionless | Sat | 2014-01-01 | 2014-12-31 | Hourly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse Office Activity Schedule | Activity | ActivityLevel | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 131.85
Warehouse Office_Plug_SCH | Unknown | Dimensionless | Default | 2014-01-01 | 2014-12-31 | Constant | 0.3
Warehouse Office_Plug_SCH | Unknown | Dimensionless | WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0
Warehouse Office_Plug_SCH | Unknown | Dimensionless | SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
Warehouse Office_Plug_SCH | Unknown | Dimensionless | Sat¦Wkdy | 2014-01-01 | 2014-12-31 | Hourly | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse ZoneControlSchedule | Unknown | ControlMode | Default¦WntrDsn¦SmrDsn | 2014-01-01 | 2014-12-31 | Constant | 1
OfficeMedium VAV Operation | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV Operation | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0%
OfficeMedium VAV OA Damper | Operation | Dimensionless | Default¦SmrDsn | 2014-01-01 | 2014-12-31 | Hourly | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0%
OfficeMedium VAV OA Damper | Operation | Dimensionless | Sat¦Sun¦WntrDsn | 2014-01-01 | 2014-12-31 | Constant | 0%