## Instructions
Instruction Sheet
Worksheet Name | Instructions to 4 Wing | 4 Wing check off after item has been reviewed | 4 Wing Comments / note if information is unavailable
Simulation Assumptions | Please review tab Simulation Assumptions. Provide any comments in column C.
Proposed Energy Conservation Measures | Please review tab Proposed Energy Conservation Measures (ECMs). Provide any comments in column P.
District Heating | Please review tab District Heating tab and provide answers to the questions at the bottom and right.
Demolition and New Construction | Please review tab Demolition and New Construction, verify the lists and provide answers to the questions in yellow.
Costs | Please review tab Costs and provide answers or comments.
Planning | Please review tab Planning and provide answers or comments.
Additional Questions for 4 Wing
Mobile / Pre-Fabricated type buildings | Could 4 Wing please provide us a list of these types of buildings with PRIN number and address? And if possible heating fuel type?

## Infiltration Rates Reference
Air Leakage (Infiltration) Rate Assumptions
Units are = m3/s/m2
Infiltration Building Type | 2005-2014 | 1980-2004 | 1960-1979 | pre-1960
Air Terminal | 0.0002 | 0.00035 | 0.0005 | 0.0007
Communications & Control | 0.0002 | 0.00035 | 0.0005 | 0.0007
Control Tower | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fire Hall | 0.0003 | 0.00045 | 0.00075 | 0.0008
Fitness & Rec. - Arena | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Multi-gym | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Pool | 0.0002 | 0.00035 | 0.0005 | 0.0007
Food Services | 0.0002 | 0.00035 | 0.0005 | 0.0007
Hangars | 0.0003 | 0.00045 | 0.00075 | 0.0008
Infrastructure | 0.0003 | 0.00045 | 0.00075 | 0.0008
Medical Facilities | 0.0002 | 0.00035 | 0.0005 | 0.0007
Misc. Bldgs < 100m2 | 0.0002 | 0.00035 | 0.0005 | 0.0007
Mobile Prefab Buildings | 0.0002 | 0.00035 | 0.0005 | 0.0007
Motel Type Residences | 0.0002 | 0.00035 | 0.0005 | 0.0007
Museum | 0.0002 | 0.00035 | 0.0005 | 0.0007
Offices | 0.0002 | 0.00035 | 0.0005 | 0.0007
Recreational / Club Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Religious Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Retail Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Sleeping barracks | 0.0002 | 0.00035 | 0.0005 | 0.0007
Storage Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Training Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
University Dormitory Type | 0.0002 | 0.00035 | 0.0005 | 0.0007
Warehouses | 0.0003 | 0.00045 | 0.00075 | 0.0008
Workshops | 0.0003 | 0.00045 | 0.00075 | 0.0008
Small Building Types | [5 empty] | Infiltration @ 5 pascals (normal)
Bldg Type | Type | No. Bldgs | Ave. Floor Area (m2) | Total Area (m2) | % Total Floor Area | pre-1960 |  | 1960-1979 |  | 1980-2004 |  | post-2004
[6 empty] | ACH | L/s/m2 | ACH | L/s/m2 | ACH | L/s/m2 | ACH | L/s/m2
Hangars | 1c | 3 | 435 | 1305 | 3.687% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Training Bldgs | 2b | 3 | 292.2 | 876.6 | 2.477% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Warehouses (Sheds) | 3b | 30 | 382.4 | 11472 | 32.41% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Sleeping barracks | 4c | 15 | 133.8 | 2007 | 5.67% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Recreational / Club Bldgs | 5d | 10 | 300.6 | 3006 | 8.492% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Offices | 6b | 11 | 323.8 | 3561.8 | 10.06% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Food Services | 7b | 2 | 290.8 | 581.6 | 1.643% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
(new) Storage Bldgs | 8b | 16 | 310 | 4960 | 14.01% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Workshops | 9b | 6 | 240.1 | 1440.6 | 4.07% | 1.5 | 0.8 | 1 | 0.75 | 0.66 | 0.45 | 0.4 | 0.3
Medical Facilities | 10b | 1 | 278.7 | 278.7 | 0.7874% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Retail Bldgs (+ Retail/Office) | 11b | 1 | 407 | 407 | 1.15% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Communications & Control | 13c | 6 | 260.6 | 1563.6 | 4.417% | 1 | 0.7 | 0.6 | 0.5 | 0.44 | 0.35 | 0.27 | 0.2
Misc. Bldgs < 100m2 | 15 | 162 | 24.3 | 3936.6 | 11.12% | 1.0 (0.70) | 0.7 | 0.6 | 0.5 | 0.44 (0.35) | 0.35 | 0.27 | 0.2
|  |  |  | 35396.5 | 100%
Percentage of total building area represented by Part 9 |  |  |  | 10.5%
|  | 104 |  | 31459.9
Part 3 Building Types | [5 empty] | Infiltration @ 5 pascals (normal)
Bldg Type | Type | No. Bldgs | Ave. Floor Area (m2) | Total Area (m2) | % Total Floor Area | pre-1960 |  | 1960-1979 |  | 1980-2004 |  | post-2004
[6 empty] | ACH (L/sec/m2) |  | ACH (L/sec/m2) |  | ACH (L/sec/m2) |  | ACH (L/sec/m2)
Hangars | 1a | 9 | 9710.5 | 87394.5 | 28.98% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Air Terminal | 1b | 1 | 3086 | 3086 | 1.023% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Training Bldgs | 2a | 4 | 4204.6 | 16818.4 | 5.576% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Warehouses (Storage Bldgs) | 3a | 8 | 2202.6 | 17620.8 | 5.842% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Motel Type Residences | 4a | 2 | 4497.6 | 8995.2 | 2.982% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
University Dormitory Type | 4b | 5 | 2814.6 | 14073 | 4.666% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Sleeping barracks | 4c | 4 | 710 | 2840 | 0.9416% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Multi-gym | 5a | 2 | 3119.1 | 6238.2 | 2.068% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Arena | 5b | 1 | 3414.4 | 3414.4 | 1.132% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fitness & Rec. - Pool | 5c | 1 | 3042.2 | 3042.2 | 1.009% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Offices | 6a | 14 | 3549.7 | 49695.8 | 16.48% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Food Services | 7a | 3 | 4701.9 | 14105.7 | 4.677% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Infrastructure (former Garage & Process Enclosures) | 8a | 2 | 808.1 | 1616.2 | 0.5359% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Workshops | 9a | 20 | 2696.1 | 53922 | 17.88% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Medical Facilities | 10a | 1 | 3344.5 | 3344.5 | 1.109% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Retail Bldgs | 11a | 2 | 1576.9 | 3153.8 | 1.046% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Religious Bldgs | 12 | 1 | 1169.2 | 1169.2 | 0.3876% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Control Tower | 13a | 1 | 1294 | 1294 | 0.429% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
Fire Hall | 13b | 1 | 1146.54 | 1146.54 | 0.3801% | 1.5 (0.80) |  | 1.0 (0.75) |  | 0.66 (0.45) |  | 0.40 (0.30)
Museum | 14 | 1 | 8643.7 | 8643.7 | 2.866% | 1.0 (0.70) |  | 0.60 (0.50) |  | 0.44 (0.35) |  | 0.27 (0.20)
|  | 83 |  | 301614.14 | 100%
Note: Values Taken and Adapted from: (1) U.S. Army Corps of Engineers " Building Air Tightness: Army Requirements and Case Studies (New Construction and Retrofit Projects)"
7th Annual Workshop, Energy Efficient Technologies for Buildings and Communities, Jan 28, 2011 Las Vegas
(2) "Air Barrier Test Results and Trends: Experience from 100+ Buildings" Pie Forensic Consultants, presented at Energy Efficient Technologies for Buildings and Communities, Jan 28, 2011 Las Vegas
(3) "Efficient Technologies to Reduce Building Energy Use and Meet Federal Requirements, Alexender Zhivov, U.S. Army Corps of Engineers
Mobile/Pre-Fabricated archetype | 0.27 ACH (0.20 L/s/m2)
Note on K35: mlubun: ASHRAE 90.1 1999 value
Note on G37: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I37: mlubun: 50% increase in ACH and leakage due to door openings
Note on K37: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M37: mlubun: 50% increase on ACH and leakage due to door openings
Note on G39: mlubun: 50% increase due to hanger door openings
Note on I39: mlubun: 50% increase in ACH and leakage due to door openings
Note on K39: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M39: mlubun: 50% increase on ACH and leakage due to door openings
Note on G45: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I45: mlubun: 50% increase in ACH and leakage due to door openings
Note on K45: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M45: mlubun: 50% increase on ACH and leakage due to door openings
Note on K57: mlubun: ASHRAE 90.1 1999 value
Note on G59: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I59: mlubun: 50% increase in ACH and leakage due to door openings
Note on K59: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M59: mlubun: 50% increase on ACH and leakage due to door openings
Note on G62: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I62: mlubun: 50% increase in ACH and leakage due to door openings
Note on K62: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M62: mlubun: 50% increase on ACH and leakage due to door openings
Note on M69: building renovated in 2005.
Note on G71: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I71: mlubun: 50% increase in ACH and leakage due to door openings
Note on K71: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M71: mlubun: 50% increase on ACH and leakage due to door openings
Note on G72: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I72: mlubun: 50% increase in ACH and leakage due to door openings
Note on K72: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M72: mlubun: 50% increase on ACH and leakage due to door openings
Note on G77: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I77: mlubun: 50% increase in ACH and leakage due to door openings
Note on K77: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M77: mlubun: 50% increase on ACH and leakage due to door openings

## Simulation Assumptions
Input Assumptions for Building Energy Models
Computer simulation models were used to estimate the energy usage in buildings. Simulation models predict the energy consumption and interaction of building systems. 11 buildings have been modelled and will represent the other similar building types - 'archetypes' - throughout the Base. This document lists the inputs or assumptions that were used in the computer models. Wherever possible, the actual equipment, occupancy, schedules and operating values were used in the models. Otherwise, assumptions were based on typical values from the Canadian building code, known as the Model National Energy Code for Buildings (MNECB).
Item | Canmet Energy's Assumptions and Values | 4 Wing Comments?
Weather (historical weather data) | Edmonton average weather data. A data file called Canadian Weather year for Energy Calculation (CWEC)
Occupancy
number of occupants in buildings | Building Code values adjusted for the actual occupancy reported in the audit
occupancy schedules in buildings | actual schedules reported in the audit
Building Construction
insulation levels in walls and ceilings | estimated from the building plans, including renovations to walls and roofs (see attached sheet 'R-values')
air tightness / air leakage | estimated from a U.S. Army Corps of Engineers study (see attached sheet 'Infiltration Rates')
Lighting
type of lamps | metal halides in the bay spaces of recreation centres, storage buildings, workshops, and hangars. Otherwise all T8 fluorescents
lighting density (Watts/m2 of floor area) | Building Code values used to estimate the number of lamps per square metre of floor area
contribution to space heating | In most spaces, lights generate heat that contributes to useful space heating and also contributes to summer cooling loads. This is not the case in bay spaces where the heat from lights does not reach occupants.
schedule | Same as building occupancy schedule reported in the audit
Plug Loads
plug loads (Watts/m2 of floor area) | Building Code values
schedule | Building Code values
Heating Equipment
heating system capacity | auto-sized by the computer model based on heat loss calculation and design temperatures
AHU and RTU heating side efficiency | actual if available, otherwise 80% for direct fired equipment
space temperature setpoint | 21 °C average assumed for all buildings and spaces
boiler capacity | auto-sized by the computer model
boiler efficiency | actual if available, otherwise 80%. 80% estimated for central plant heated buildings
hot water setpoint | 82 °C
boiler with outdoor air reset control | installed in central plant heated buildings; not installed in other buildings
nighttime temperature setback | not currently practiced in any buildings
HVAC night control | assume zone thermal units (if applicable) can cycle on to meet heating setpoint. may be fan coil, terminal unit, baseboard, or RTU
Main Heating Pumps
flow capacity and horsepower | auto-sized by the computer model
pump motor efficiency | adjusted according to age of building
pump speed | constant, single-speed
Cooling Equipment
cooling system capacity | auto-sized by the computer model based on heat loss calculation and design temperatures
space temperature setpoint | 24 °C average for cooled spaces
cooling efficiency | the coefficient of performance (COP) for cooling equipment and air conditioners is corelated to building age: 2.5 for systems pre-1980; 3.0 for 1980-2004; 3.5 post-2004
spaces with cooling | cooling is assumed for spaces with occupants only, for example in offices but not in storage spaces; also based upon actual information from audits
free cooling economizers | assume economizers are installed and operating in all AHUs and RTUs
Ventilation | including AHUs, MUAs, RTUs, exhaust fans, ceiling fans, transfer air fans
fan capacity and horsepower | auto-sized by the computer model. Fan power is estimated separately for supply, return and exhaust fans using typical static pressure of AHUs
fan speed | constant speed
fan motor efficiency | adjusted according to age of building
ventilation fresh air requirement | Building Code outdoor air per person rates, and occupancy levels from audit
ventilation schedule | always on (assumption is the heating and cooling setpoints are met, and fresh air requirement for number of occupants only). Ventilation runs through the night same as daytime
exhaust fans capacity and schedule | actual values reported in audit, otherwise assume 24 hour operation
Domestic Hot Water
peak flow and temperature | based on Building Code values for temperature, litres and draw profiles
water tank capacity | Building Code value
water tank efficiency | actual if available otherwise 80% for gas-fired, 100% for electric with standby losses taken into account separately
schedule | based on predominant Building Code space type
water heater pumps | horsepower autosized by computer model; runs constantly
fuel type | based on audit
Miscellaneous
humidification/dehumidification | no humidification is assumed; dehumidification accounted for by cooling
combining systems | separate HVAC equipment was sometimes combined in order to simplify computer modelling
HVAC system type v.s. age of building? | the type of HVAC equipment was not correlated to the building's age because buildings have undergone so many retrofits and added new heating and ventilation systems
Firehall | use Trenton Firehall and run with Edmonton weather data. The Cold Lake Firehall is the same building design as Trenton's.
B172 CF18 Training | use Trenton Training archetype building and run with Edmonton weather data. No building plans were made available by Cold Lake for this building.

## Proposed ECMs
Proposed Energy Conservation Measures for Buildings
| Type | Energy Conservation Measure Name | Short Description of ECM | Controls Based | Interaction of ECMs | How Modelled? | Costed? | Cost Units | Reference or Source for assumptions | Long Description of ECM / for Modelling | Cold Lake Audit Notes (Matthew's) | Comments | Application Rate | Implementation | Miscellaneous / Other Benefits | 4 Wing Comments?
1 | Ventilation | Occupancy control for exhaust fans | A sensor determines when a space is unoccupied and the control shuts off exhaust fans and make-up air units (MUA). Saves fan energy (electricity) and heating. | yes |  | not modelled for Trenton. could be modelled in OS | yes |  | Followed the MNECB or real schedule for fan operation | same as short description |  | Seems to pay back well on a ½ h.p. fan running 24/7. Phylroy would need to schedule exhaust fans distinctly from air handlers | % of buildings or floor space this ECM applies to
2 | Ventilation | Demand controlled ventilation (DCV) control | Minimizes the delivery of ventilation air by measuring the carbon dioxide concentration in the space, and delivering enough air to meet the building code. Installed in AHUs and RTUs. Saves on fan energy and heating. | yes | overlap with VFD. Increases heating | OS | yes. Did not include the cost of a VFD |  | MNECB 1997 schedules for fan operation, or real schedule | Adjusts the rate of ventilation air delivered to a space by measuring the carbon dioxide concentration in the space. When there are no occupants in the space, ventilation is minimized, saving on fan energy. Two types of demand control ventilation devices assessed: sensors in occupied spaces controlling airflow to the space and sensors in return air duct controlling operation of the air handler. | I observed strong ventilation running in the REC Centre squash courts and activities room while unoccupied. | Risk of comfort problems according to staff. Building specific. Should package DCV with VFD ECM. | % of buildings or floor space this ECM applies to | Control prioritizes space temperature before ventilation. Must not interfere with existing pre-cooling practice. For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%. | Where mechanical cooling is undersized, this ECM would keep buildings cooler by reducing the addition of warm outdoor air during summer
3 | Ventilation | Variable frequency drive (VFD) control for air handler fans | A VFD adjusts the fan speed to match the actual need for ventilation air, heating or cooling. Installed in constant speed AHUs and RTUs. This saves on fan energy, heating and cooling. | yes | overlap with DCV. Increases heating | OS | yes |  | Assume existing fans have constant speed, based on MNECB 1997. We will assume a typical fan type curve. | For constant speed AHUs and RTUs, a controller which measures the return air/outdoor air temperatures and adjusts the fan motor to maintain a return air temperature or to adjust the volume of air delivered to maintain return air temperature and/or carbon dioxide in return air stream. A 20% lower fan speed saves 50% of the fan energy. Also reduces the cost to condition outside air. | Some AHU fans have VFDs (REC Centre has at least one AHU). They can be problematic according to Rob Williams | Needed for DCV. Can program VFD to respond to duct static pressure, zone temperature, or CO2 concentration. | % of buildings or floor space this ECM applies to | For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%.
4 | Plug Loads | Occupancy sensor control for plug loads | A PIR + ultrasonic sensor turns on a circuit for wall plugs when it is activated by a person entering the room. After the occupant leaves the room and there is no activity sensed, a timer turns the circuit off, saving on electricity. | yes |  | manual | yes |  | MNECB 1997 by space type | same as short description | Many personal heaters and fans are used in offices. This ECM could ensure they are being shut off at night, as well as computers and office equipment. |  | % of buildings or floor space this ECM applies to
5 | Lighting | Replacement of T8 lamp fixtures with T5s | Replace existing T8 and T12 fixtures with dimmable T5 fixtures. This saves approximately 30% on electricity. | no | increases heating, reduces cooling | OS with a manual factor of 30%. Used W/m2 in model and no fixture counts | yes |  | MNECB 1997 by space type | Lighting energy was reduced by 30% over MNECB energy levels per space by assuming existing T8 fluorescent fixtures in offices, barracks, warehouses). |  | Lighting contributes useful space heating in some spaces and conversely adds to cooling loads. In high bay spaces it is assumed not to contribute to space heating. | % of buildings or floor space this ECM applies to
6 | Lighting | Replacement of metal halide lamp fixtures with T5s | Replace existing 400W or 250W Metal Halide lamps with high-intensity, instant start, T5 fixtures. This saves approximately 50%. | no | increases heating, reduces cooling | OS with a manual factor of 30%. Used W/m2 in model and no fixture counts | yes |  | MNECB 1997 by space type | Lighting energy was reduced by 30% over MNECB energy levels per space by assuming existing metal halide fixtures (400W) in hangers and workshops and metal halide fixtures (250W) in gyms and recreational high bay spaces | various wattages of metal halides were observed. | Assume same floor area application as Trenton. Set HIDs to 5% space heat. Note other benefits of fluorescent e.g. lumen depreciation | % of buildings or floor space this ECM applies to |  | Alert Hangars with metal halide lights left on 24/7 could potentially turn off fluorescents if they are instant start. Since metal halides takes time to warm up they are currently left on at all times.
7 | Lighting | Occupancy sensor control for lighting | A PIR + ultrasonic sensor turns on a circuit for lights when it is activated by a person entering the room. After the occupant leaves the room and there is no activity, a timer turns the circuit off, saving on electricity. | yes | increases heating, reduces cooling | not modelled for Trenton | yes, same sensor used for plug loads |  | MNECB 1997 by space type | same as short description | could apply to workshops, mechanical rooms, bathrooms – tend to be infrequently occupied | Include a paragraph on photocells for outdoor lighting | % of buildings or floor space this ECM applies to
8 | Heating | Upgrade of pump and fan motors | Replace standard efficiency pump and fan motors with NEMA rated Premium efficiency motors. Saves in the order of 5% of electricity. | no | increases heating | not modelled for Trenton. could be modelled in OS | yes |  | Start with MNECB 1997 values | same as short description |  | Need to assume efficiency of typical existing motor | % of buildings or floor space this ECM applies to | This could be part of a motor replacement program or a regular maintenance plan. Staff could use Motormaster.com software to inventory and select motors
9 | Heating | Outdoor air temperature reset control for hot water loop | A controller that measures the outdoor air temperature and raises or lowers the hot water loop temperature to better match the building heat loss. It saves energy by minimizing heat loss in the distribution and boiler stack since the boiler cycles less often. | yes | VSD on pumps | not modelled for Trenton. could be modelled in OS. To be determined | yes |  | NECB 2011 sequence for boilers | A hot water reset control measures the outside air temperature; this information is used to estimate the building heating load as the outdoor temperature varies. The supply hot water temperature is modulated up and down range in an inverse linear ratio to outside air temperature. The typical range for conventional boilers is to vary the supply water temperature from 60 .. 82 ⁰C as the outside temperature varies from +18 .. -18 ⁰C. | Outdoor Air Reset of Hot Water Converters: This is supposed to be currently installed in buildings heated by the DES. Was installed by MCW in 1998-2001. | REC centre has it. Assume that buildings newer than 15 year old include it. | % of buildings or floor space this ECM applies to |  | Boiler low-limit setting of 180F seems to prevent the Outdoor air reset from setting as low as it could potentially go.
10 | Heating | Variable speed drive (VSD) control for hydronic/heating pumps | A VSD varies the speed of a hydronic pump as the need for heat in the building changes. For example in warmer weather, the pump speed can be reduced. Saves on heating and pumping energy. | yes | Outdoor air reset | OS | yes |  | Assume existing pumps have constant speed, based on MNECB 1997. | VSD controller for a pump along with a 2-way valve on the hydronic loop which measures the return water temperature and adjusts the pump motor and the 2-way valve position to maintain a design temperature differential. Savings are in heating and pump energy . A 20% lower speed saves 50% of pumping energy. | Pool water pumps – base speed on pool water turbidity. This should ramp down pumping at night |  | % of buildings or floor space this ECM applies to |  | Didn’t energy model this.
11 | Heating | Supply air temperature reset control | In AHUs or RTUs, this control lowers the supply air temperature to more accurately match the space heating load, based on measuring the return air temperature. Saves on heating , cooling and re-heat energy. | yes |  | OS | yes |  | Is a standard control sequence in the NECB 2011 | In AHUs or RTUs, reduces the supply air temperature or reheat temperature based on measuring return air temperature to match the heating load more closely as indoor conditions change. Saves on heating, cooling and reheat energy. |  |  | % of buildings or floor space this ECM applies to
12 | Heating | Retro-commissioning of HVAC systems | Includes the re-calibration of thermostats and re-tuning of all the controls in AHUs and RTUs. This saves on electrical, heating and cooling energy. | no | Not to overlap with the other control ECMs | manual | yes, for two measures |  | Used ASRHAE Energy Efficiency Guides for Existing Commercial Buildings. | Re-calibrating of thermostats in occupied spaces and retuning of all of the controls within the AHUs and RTUs to ensure that the sequence of operations and settings (valve, damper, temperatures, sensors) are within design specifications | Col d Lake has a need to update the missing documentation on building controls | Empirical data is found in the PNNL 2012 Study on Commercial Building Re-tuning | % of buildings or floor space this ECM applies to |  | Zero energy dead band setpoints in heat/cool HVAC equipment so to avoid simultaneous heating and cooling …
13 | Heating | Nighttime temperature setback | Using a programmable thermostat or BAS, the space temperature is lowered by 2°C during unoccupied hours and brought back up 2°C before occupied hours. This reduces the amount of heating. | yes |  | OS | yes |  | 2°C was agreed to be reasonable | Reduction in the heating setpoint by 2°C for unoccupied hours (assumes a zero setback strategy currently exists) | Various technicians, building occupants and CE staff indicated reluctance to set back temperature at night due to previous issues with comfort, recovery time and the risk of freezing the building. There is potential in some spaces (e.g. unit heaters on thermostats). Difficulty recovering temperature in older buildings. | We could assume there is potential in 25% (?) of spaces. Due to the climate and comfort, we did not recommend the occupied hours temperature reduction recommended for Trenton. | % of buildings or floor space this ECM applies to |  | Digital programmable thermostat would be needed for Barracks with perimeter convectors and Braukmann thermostat controls.
14 | DHW Heating | Replacement of electric hot water tanks with gas-fired hot water tanks | Replacement of electric hot water tanks with gas-fired hot water tanks. This saves on energy costs and GHGs. | no |  | OS | yes |  | Assume an E.F. for the electric (EF 0.92, 100% s.s.) and for the gas hot water tank (EF 0.67. 80% s.s.). seasonal efficiency. Use MNECB 1997 daily occupant or space DHW consumption and draw profile. | Replacement of electric hot water tanks with gas-fired hot water tanks. This saves on energy costs and GHGs in Alberta since the GHG factor for natural gas is lower than the factor for electricity. | Many electric DHW tanks were observed in audited buildings |  | % of buildings or floor space this ECM applies to | Must consider the existing capacity of gas pipe and proximity of nearest gas pipe to the electric hot water tank. | because electricity is five times more expensive, consider gas-fired DHW to save operating cost and GHG emissions
15 | DHW Heating | Drainwater heat recovery for Barracks | A copper drain pipe device (a gravity film exchanger) recovers the heat - mainly from shower drainwater - and transfers it to the cold domestic water as it flows into the hot water tank. This saves on DHW heating energy. | yes |  | manual. not modelled for Trenton. There is a DWHR module in EnergyPlus | no |  | Use MNECB 1997 daily occupant or space DHW consumption and draw profile. | same as short description | Potential in the barracks. A main drainwater pipe is close by to the DHW Heater. | Matthew could estimate the cost | % of buildings or floor space this ECM applies to
16 | DES | Replacement of building steam converters with hot water heat exchangers | To accommodate a new DES using low temperature hot water, the existing steam "converters" in buildings would need to be replaced with hot water heat exchangers. | no |  | manual | yes |  | Not applicable | same as short description |  | Is this considered an "ECM"? | % of buildings or floor space this ECM applies to
17 | Cooling | Cold deck reset control | During mechanical cooling, supply air temperature is reset based upon the return air temperature and the outdoor air temperature to ensure the space does not overcool resulting in possible reheat energy. This saves on cooling energy and possibly reheat energy. | yes | impact reduced via compressor upgrade or replacement of cooling | OS | yes |  | Assuming a constant supply air temperature, as per MNECB 1997 | During mechanical cooling, supply air temperature is reset based upon the return air temperature and the outdoor air temperature to ensure the space does not overcool resulting in possible reheat energy. Savings are due to reduced mechanical cooling and some fan energy. Adjust the stages of cooling or the refrigerant valve in response to the return air temperature. Prevents over-cooling of space | Observed only DX cooling during audits |  | % of buildings or floor space this ECM applies to
18 | Cooling | Upgrade of compressors in cooling/air conditioning | Replace the compressors in cooling condensers and air conditioners with the latest energy efficient compressors. This saves on electricity. | no | overlap with replacement of cooling | OS | yes |  | Start with a COP of 2.5 in V3 and V4, and COP 3.0 in V1 and V2 based on typical MNECB 1997 values | Replacement of the AHU and RTU compressor only with a new scroll compressor (COP 4.0) using R-410A refrigerant. Existing compressors are assumed to be COP 2.5 for all pre-2004 buildings and COP 3.0 for all post-2004 buildings. | The average age of condensers is estimated to be 15 years old. | The cost to upgrade < 5 ton compressors was similar to replacing the entire outdoor section of a mini-split air conditioner. See ECM below | % of buildings or floor space this ECM applies to
19 | Cooling | Replacement of cooling section of an AHU or RTU. Or replacement of the whole RTU. | Replace the DX equipment (both the condenser section and evaporator coil) or an entire RTU with a new energy efficient model. Saves on heating, cooling and electricity through better COP, furnace efficiency and more advanced controls. | no | overlap with compressor upgrade | not modelled for Trenton. could be modelled in OS | We costed RTU total replacement, and AHU replacement. But equipment cost is likely to be similar for replacing only the DX section |  | Start with a COP of 2.5 in V3 and V4, and COP 3.0 in V1 and V2 based on typical MNECB 1997 values | Complete replacement of the direct expansion (DX) unit within an AHU or RTU, or replacing a DX/furnace RTU with a high efficiency unit. |  | Applies also to mini-split air conditioners: outdoor section would be replaced with a new higher COP model. Use the cost estimate from the compressor ECM above | % of buildings or floor space this ECM applies to | For RTUs an alternate to this ECM could be the Advanced RTU Controller 'Catalyst' that combines fan speed, economizer and DCV controls and saves 25% to 50%. The COP would not improve but everything else would.
20 | Building Envelope | Air tightening of the building envelope | Sealing or weather-stripping of roofs, walls, windows, doors, and all penetrations through the building envelope. This reduces cold air entering the building (infiltration) and warm air escaping (exfiltration). Saves on heating and cooling. | no | Reduces building heat loss, reducing impact of other heating ECMs | OS | yes |  | US Military study of blower door test results and modified to our vintages | Foaming of envelope penetrations and junctions, weather-stripping of doors to reduce leakage levels to 0.27 air changes per hour at normal pressure from the assumed leakage rates per vintage and building type. Pre-1960s buildings = 1.0 air changes per hour, 1960-1979 buildings = 0.6 air changes per hour, 1980-2004 buildings = 0.44 air changes per hour, post-2004 = 0.27 air changes per hour. If building type contained overhead doors, space containing overhead door assumed increased air leakage of 50%. |  | Is air leakage unknowingly being used for ventilation? Will a tighter building envelope affect air quality and create a need for more ventilation, thus costing more in equipment and fan power? | % of buildings or floor space this ECM applies to | A blower door test is required to determine actual conditions. Could draft proof and test buildings at the same time.
21 | REC Centre | Special/Unique ECMs for the REC Centre | Write up noting the typical measures and associated savings. Specific measures for Ice plant (floating compressor head control), IR camera for ice surface temperature, flood water treatment, pool pump turbidity-controlled VSPs, DCV during winter.ECMs that are unique to the REC Centre. The other ECMs on this sheet apply to the REC Centre. | yes |  | not modelled for Trenton. Will not model special/unique measures | no |  | MNECB, retrofit case studies, figures from Raymond’s previous study in a similar sized REC centre | same as short description | 570 kW demand noted during the audit | Rec Centre is approximately 9% of heated buildings floor area
22 | Centralized BAS Control | Control Centre for Building Automation Systems | Centralized monitoring and control of each building's BAS systems. | yes |  | not modelled | no |  | literature, case studies |  | The technician staff are interested in implementing this system before any building control-type ECMs are attempted. There would be poor acceptance without the ability to monitor the HVAC systems. There are already many comfort issues. There is resistance to alter the current control settings and not enough staff to implement, test and monitor. | Base should update the missing documentation on existing BAS systems. This would be a first step to undertaking a retro-commissioning program. Base recently hired companies to update controls in 3 buildings. MCW updated a lot of buildings controls in 2001. |  | We could cite the O&M benefits to EMS such as predictive maintenance, alarms. | Would a central BAS control save energy?

## District Heating
District Heating
Item | Canmet Energy's Assumptions and Questions | Buildings using Steam directly in their heating systems
Heating Network |  | Bldg No. | Building Name | 4 Wing please list the terminal heating equipment using steam
| · All network modelling will assume integration of a hot water distribution network (~110 °C design supply temperature), constructed over 3 phases: | H1 | Hangar 1
| Phase 1: connect to buildings currently supplied with steam from the CHP, and omitting any buildings slated to be demolished | B177 | F404 Engine Bay/Composite Bldg
| Phase 2/3: connect to buildings currently heated with individual gas-fired systems as seen practical, as well as future buildings to be constructed | H2 | Hangar 2
| · Piping assumed to be new, thin-walled steel district heating pipe (preinsulated, bonded) to be direct buried at approximately 1 metre below grade. | H4 | Hangar 4 | hangar door floor blast heaters , 2 steam coils
| · In an effort to generate conservative estimates for required network piping, analysis will be based upon the estimated base-case (pre-ECM) building heating loads and no diversity or simultaneity of network heating loads will be considered. | H3 | Hangar 3
|  | H6 | Hangar 6
Potential Central Heating Plant options |  | B171 | Supply Warehouse
| · New gas-fired hot water boilers. | B5 | WTN Garage
| · Investigate other alternative supply options including biomass boilers and cogeneration. | B7 | CE Main Bldg
| · Modelled plant to be located at or near the existing CHP building unless directed otherwise. | B63 | GSAR/Battery Shop/Supply
| · Modelled plant operation and fuel consumption analysis will factor estimated building energy reductions achieved through integration of building Energy Conservation Measures. | B66 | Supply Bldg
|  | B192 | GPV Garage
Building Network Interface |  | B8 | Exercise Support Office
| · New hot-water energy transfer stations consisting of one or more brazed-plate or flat plate heat exchangers will replace existing steam convertors in each connected building | B174 | CE Roads and Grounds Bldg
| · It is assumed that the district heating supply will provide both space heating and domestic water heating for each connected building | B81 | Electrical and Sheet Metal Shop
|  | B80 | Roundel Cleaners (NPF)
Questions for 4 Wing. Please answer below. |  | B10 | Standby Power Plant
| · Please confirm the buildings that are still using steam directly in terminal heating equipment. See list at right. Please name the terminal equipment that use steam coils. | B6 | RM Storage
|  | B128 | WOps EOD Centre # 19
· If known, please provide potential time horizon for any planned changes to the existing steam network and CHP
· Also confirm if there are any other specific buildings on the Base that should be excluded from the district heating system modelling?
· Do any of the buildings currently connected to the steam network have thermal meters installed? If so, can data be provided?
· Any additional directional information to consider in the analysis – items Cold Lake personnel would like to see included or not included in the analysis?

## Demolition and New Construction
Demolitions and New Construction
Planned for Demolition - 4 Wing please verify and update
Bld: PRIN Number | Bld: PRIN Name | Bld: PRIN Address | demo/replacement date
22122 | Hangar 1 | H1 - Hangar Lane | to be replaced 2022 w 5000 sq.ft.
22123 | Hangar 2 | H2 - Hangar Lane | to be replaced 2021 w 6000 sq.ft.
22124 | Hangar 3 | H3 - Hangar Lane | to be replaced 2019 w 6000 sq.ft.
22126 | Hangar 6 | H6 - Hangar Lane | to be replaced 2017 w 6000 sq.ft.
22129 | Fire Hall | B4 - Athabasca Road | to be demolished
22146 | Officers Mess | B20-Timberline Drive | to be demolished
22153 | NCO Mess | B30 - Queensway | to be demolished
22156 | All Ranks Mess | B40-Queensway | to be demolished
22157 | Club 41 | B41-Beaverlodge Road | to be demolished
22167 | RC Chapel | B53-Queensway | to be demolished
63089 | Maple Flag Quarters 1 or storage building | B165 - Kingsway | to be demolished
63090 | Maple Flag Quarters 2 or storage building | B166 - Kingsway | to be demolished
Planned New Buildings - 4 Wing please verify and update
construction year | name | location | gross floor area, sq.m | Does it replace an existing building?
2011 | 100 p. accomodation | beside trimess | 5000
2011 | 100 p. accomodation | beside trimess | 5000
2011 | 100 p. accomodation | beside trimess | 5000
2011 | school/daycare | @B82 | 7500
2012 | firehall | beside H7 | 1500
2012 | RTF | beside B84
2013 | trimess | between B20,30,40 | 4000
2013 | Canex | across from B69 | 10000
2014 | airport tower | south of H1 | 500
2014 | chapel |  | 600
2015 | 100 apartmt (750sq.ft ea) |  | 7500
2017 | Hangar 6 | H6 - Hangar Lane | 6000 | replaces Hangar 6
2019 | Hangar 3 | H3 - Hangar Lane | 6000 | replaces Hangar 3
2021 | Hangar 2 | H2 - Hangar Lane | 6000 | replaces Hangar 2
2022 | Hangar 1 | H1 - Hangar Lane | 5000 | replaces Hangar 1
Canmet Energy's Questions
Are there Energy intensity performance targets for new buildings?
Are any buildings anticipated to undergo major changes of use? If so, which ones, what will their use by changed to?

## Costs
Cost Assumtpions
Item | Canmet Energy's Assumptions and Values | 4 Wing Answers / Comments?
Utility Costs
historical rates | historical rates for electricity and natural gas were provided by DND
future rates | Carmal rate forecast for electricity. Gas Alberta forecast for natural gas
Labour Rates (to be used in Payback calculations)
electrician, plumbers, controls technician, insulation contractor, air sealing contractor, and all general labor | $60 per hour
design services | $100 per hour
4 Wing's Budget for Buildings and Infrastructure
Annual budget allocated for Building O&M | ?
Annual budget allocated for building and infrastructure renovations | ?
Annual budget allocated specifically for energy retrofits | ?
Annual budget allocated for new buildings and new infrastructure | ?
Projected annual growth rate of above budgets | ?
New
Projected utility rates for electricity, natural gas and other sources
broken down for each year of the planning horizon
Projected inflation for capital costs for retrofits
broken down for each year of the planning horizon
Projected emissions factors by energy source
May change for electricity due to anticipated supply mix
Planning Horizon
- what are the next two business cycles? (18-19 - 22-23) How many years does mid-long range planning on the base typically look out to?
Additional qualitative questions important for the planning context
- Specific environmental policies, targets or reports of which we should be aware?
- Is there any linkage between planning on the base and that being done in surrounding communities?
- Level of senior level buy-in for energy efficiency/renewable energy technology measures?
- Perception of acceptance of energy efficiency/renewable energy technology measures by Base personell?

## Planning
Planning for Buildings and Infrastructure
Item | Canmet Energy Assumptions and Values | 4 Wing Answers / Comments?
Planning Horizon
What are 4 Wing's five year business cycles? (2018-19, 2022-23?) | ?
How many years does mid-long range planning for 4 Wing typically look out to? | ?
GHG Emissions
Federal Sustainable Development Strategy GHG reporting data back to 2005-06 (GHG emissions baseline year). Does 4 Wing have this data? | ?
Planning and Environmental Policies
Relevant Policies. Are there other policies, not listed here, related to planning, environment or energy? | Canada First Defence Strategy, Defence Renewal Charter, 4 Wing Mission and Vision, Federal Sustainable Development Strategy, Pan-Air Force Environmental Sustainability Plan, Air Force Sustainability Office Five Year Plan, Defence Operational Energy Strategy, Canadian Armed Forces Administrative Order 29-7
How does 4 Wing interact/co-ordinate with the Cold Lake community for its land use or other planning? How are Cold Lake community plans linked with 4 Wing's plans? | ?
Who are the Officers at 4 Wing who are responsible for or handle energy efficiency and GHG emissions? | ?

## Project team - assumptions
Cold Lake modelling assumptions
Weather file | Edmonton CWEC
Use CWEC; perhaps do a comparison to year using for analysis
Occupancy
Loads | MNECB defaults; adjusted for actual occupancy as per audit
Schedule | Actual as per audit or MNECB
Envelope | R values by building type and vintage (see sheet 'Cold Lake R-values') | scripting
Use metal cladding construction
Set R-values for trailer archeype (not based on vintage) (see sheet 'Cold Lake R-values')
no wall retrofit measures (based on trenton, not cost-effective), perhaps only roof ecms
Infiltration | Rate by building type and vintage (see sheet 'Infiltration Assumptions') | scripting
bay doors | increase infiltration rate by 50% when doors are opened (see audit info)
Lighting
Loads | MNECB defaults; some audit information available | Question: ask base contact about when lighting retrofits were done; provide MNECB default and ask if that is in the ball park.
Heat to space | Set based on building type; to be determined | Check if detailed lighting plans available for exemplar buildings; need to check if these were implemented
Schedule | Same as occupancy schedule as per audit or MNECB default by space type
Equipment
Loads | MNECB defaults; do we take into account loads in server rooms? | no; we will not tackle process loads
Schedule | MNECB defaults
HVAC
heating system capacity | auto-sized
cooling system capacity | auto-sized
cooling | for spaces with occupants only (example offices, but not storage spaces); set up systems appropriately (system with no cooling for zones with no cooling)
combine HVAC systems | yes
modify HVAC system by vintage | no
put cooling in exemplar with no cooling if other buildings for this archetype have cooling
economizers | assume in all base case models for buildings with cooling
exhaust fans | explicitly model. This is necessary if we look at exhaust fan ecm - modify exhaust fan schedule to determine impact.
humidification/dehumidification | no for humidification; dehumidification accounted for by cooling
ventilation | MNECB outdoor air per person rates
heating setpoint | Set to 21C
cooling setpoint | Set to 24C
temperature setback | not in base model
boiler with outdoor air reset | not in base model; consider as ECM | assumed to exist in DES heated buildings
boiler capacity | auto-sized
boiler efficiency | actual if available, 80% for DES systems
boiler setpoint | 82C | script
des | Des represented by boiler with 80% efficiency
HVAC system heating efficiency | actual, if available or use 80% default
HVAC system cooling efficiency | vintage COP: 2.5 for systems pre-1980; 3.0 for 1980-2004; 3.5 post-2004 | script; set base model to 2.5
fan schedule | as per audit; if no information assume always on
fan motor efficiency | see | script
fan type | constant
hvac ventilation schedule | always on
hvac night control | assume zone thermal units (if applicable) can cycle on to meet heating setpoint
pump motor efficiency | by vintage; see Mike | script
pump type | constant single-speed
system heating sizing factor | 1.1 | script
system cooling sizing factor | 1.25 | script
zone heating sizing factor | 1 | script
zone cooling sizing factor | 1 | script
plant heating sizing factor | 1.3 | script
SWH
peak flow | based on MNECB default of W/person, actual occupancy and 44C temperature difference
water tank capacity | default size
water tank efficiency | actual if available otherwise 80% for fuel-fired; 100% for electric (standby losses taken into account separately)
schedule | based on default for predominant MNECB space type
water heater pump | constant
fuel type | based on audit
hot water setpoint temperature | 60C | script
Utility costs | use time of use rate for one base case model- office; compare to result with average rate
rates, see Matthew
take into account demand and consumption charges
Simulation outputs
Yearly
load versus consumption | EUI based on energy (versus consumption); analysis will use load values and assume system efficiency
also compile #s based on consumption to compare
EUI | by end-use/fuel-source
Hourly |  | scripting
Cooling Coil Total Cooling Rate
Cooling Coil Electric Power
Heating Coil Air Heating Rate
Heating Coil Heating Rate
Heating Coil Gas Rate
District Heating Hot Water Rate
District Heating Rate
Water Heater Heating Rate
Water Heater Gas Rate
Water Heater Electric rate
Plant Supply Side Heating Demand Rate
Boiler Gas Rate
Facility Total HVAC Electric Demand Power
Facility Total Electric Demand Power
Zone Air Temperature
Demand | once ecm package is finalized, re-run archetypes to get combined demand/energy savings
Exempler model verification | do not reconcile exemplar with metered data at this point; may do this once all archetypes rolled up at base level
electric meter | tolerance? | example: | B688 ammunition maintenance facility
natural gas meter | tolerance? |  | electricity | natural gas
compare to trenton EUI for same building type? |  | metered | 278-368 GJ | 1023-1492 GJ
|  | simulation | 328 GJ | 689 GJ | note this is for setpoint 18C
baseline year | 2013-14 if utility data available for this fiscal year |  |  | 882 GJ | if setpoint is changed to 20C
Firehall archetype | use Trenton archetype and run with Edmonton weather data
B172 CF18 Training archetype | use Trenton archetype and run with Edmonton weather data
ECMs
Individual ECMs | see sheet ''
payback
combinations
Applying ECMs
applying ECM modelling results to buildings corresponding to archetype/vintage based on percentage | different percentages for more aggressive scenarios
New construction | assume no new construction

## cl_modelling_assumptions
measure_id | building_type | vintage_name | base_model_file_name | building_source | building_count | total_floor_area | building_heated_floor_area | de_heated_area | heating_sched_name | heating_setpoint_schedule | cool_sched_name | cooling_setpoint_schedule | construction_library_file | default_construction_set | ext_wall_rsi | ext_floor_rsi | ext_roof_rsi | ground_floor_rsi | ground_wall_rsi | ground_roof_rsi | fixed_window_rsi | operable_window_rsi | door_construction_rsi | glass_door_rsi | overhead_door_rsi | infiltration_building_type | infiltration_rate | cop | fan_motor_eff | fan_total_eff | pump_eff | economizer_control_type | economizer_control_action_type | economizer_maximum_limit_dry_bulb_temperature | economizer_maximum_limit_enthalpy | economizer_maximum_limit_dewpoint_temperature | economizer_minimum_limit_dry_bulb_temperature | heating_sizing_factor | cooling_sizing_factor | zone_heating_sizing_factor | zone_cooling_sizing_factor | shw_setpoint_sched | shw_heating_type | shw_thermal_eff | hw_boiler_fuel_type | hw_boiler_design_water_outlet_temperature | hw_boiler_thermal_eff
Barracks_pre-1960 | Barracks | pre-1960 | barracks.osm | B45 | 5 | 20067 | 20067 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Motel Type Residences | 0.0007 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Fire Hall_pre-1960 | Fire Hall | pre-1960 | fire_hall.osm | Trenton FH B19 | 1 | 1289 | 0 | 1289 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.1701 | 6.5164 | 6.5164 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Fire Hall | 0.0008 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Food Service_pre-1960 | Food Service | pre-1960 | food_service.osm | B40 | 4 | 10012 | 10012 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.5224 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Food Services | 0.0007 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Hangar_1960-1979 | Hangar | 1960-1979 | hanger.osm | Hangar 4 | 2 | 6231 | 6231 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 2.1134 | 1.7612 | 1.7612 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Hangars | 0.00075 | 2.5 | 0.823 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Hangar_1980-2004 | Hangar | 1980-2004 | hanger.osm | Hangar 4 | 1 | 6551 | 6551 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Hangars | 0.00045 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Hangar_pre-1960 | Hangar | pre-1960 | hanger.osm | Hangar 4 | 6 | 62176 | 62176 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.4089 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Hangars | 0.0008 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Maintenance Shop_1980-2004 | Maintenance Shop | 1980-2004 | maintenance_shop.osm | B581 | 3 | 10986 | 10986 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Workshops | 0.00045 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Maintenance Shop_pre-1960 | Maintenance Shop | pre-1960 | maintenance_shop.osm | B581 | 2 | 3983 | 3983 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Workshops | 0.0008 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Maintenance Shop-Small_1960-1979 | Maintenance Shop-Small | 1960-1979 | maintenance_shop_small.osm | B688 | 3 | 724 | 724 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Workshops | 0.00075 | 2.5 | 0.823 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Maintenance Shop-Small_1980-2004 | Maintenance Shop-Small | 1980-2004 | maintenance_shop_small.osm | B688 | 10 | 4869 | 4869 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.1701 | 4.2268 | 4.2268 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Workshops | 0.00045 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Maintenance Shop-Small_pre-1960 | Maintenance Shop-Small | pre-1960 | maintenance_shop_small.osm | B688 | 4 | 1565 | 1565 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 0.88059 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Workshops | 0.0008 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office_1960-1979 | Office | 1960-1979 | office.osm | B007 | 2 | 3480 | 3480 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Offices | 0.0005 | 2.5 | 0.823 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office_1980-2004 | Office | 1980-2004 | office.osm | B007 | 9 | 17683 | 17683 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.00035 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office_pre-1960 | Office | pre-1960 | office.osm | B007 | 6 | 15697 | 15697 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 2.8179 | 2.8179 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Offices | 0.0007 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office-Small_1960-1979 | Office-Small | 1960-1979 | office_small.osm | B96(Trailer) | 5 | 1148 | 1148 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 1.4089 | 1.4089 | 1.0567 | 1.0567 | 1.0567 | 0.28179 | 0.28179 | 0.52836 | 0.28179 | 1.4089 | Offices | 0.0005 | 2.5 | 0.823 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office-Small_1980-2004 | Office-Small | 1980-2004 | office_small.osm | B96(Trailer) | 24 | 4356 | 4356 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.00035 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Office-Small_2005-2014 | Office-Small | 2005-2014 | office_small.osm | B96(Trailer) | 7 | 501 | 501 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Offices | 0.0002 | 3.5 | 0.879 | 0.8 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Recreation Center_1980-2004 | Recreation Center | 1980-2004 | recreation_center.osm | B720 | 1 | 20880 | 20880 | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fitness & Rec. - Multi-gym | 0.00035 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Storage Building_1960-1979 | Storage Building | 1960-1979 | storage_building.osm | B782 | 9 | 2092 | 832 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.9373 | 1.5851 | 1.5851 | 1.2328 | 1.2328 | 1.2328 | 0.45791 | 0.45791 | 0.70447 | 0.45791 | 1.5851 | Storage Bldgs | 0.0005 | 2.5 | 0.823 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Storage Building_1980-2004 | Storage Building | 1980-2004 | storage_building.osm | B782 | 38 | 16364 | 10100 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 2.6418 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Storage Bldgs | 0.00035 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Storage Building_2005-2014 | Storage Building | 2005-2014 | storage_building.osm | B782 | 4 | 1431 | 502 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Storage Bldgs | 0.0002 | 3.5 | 0.879 | 0.8 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Storage Building_pre-1960 | Storage Building | pre-1960 | storage_building.osm | B782 | 6 | 1071 | 330 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 0.88059 | 3.5224 | 3.5224 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Storage Bldgs | 0.0007 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Training Building_1980-2004 | Training Building | 1980-2004 | training_building.osm | Trenton Training B34 | 1 | 4831 | 4831 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 3.5224 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Training Bldgs | 0.00035 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Training Building_2005-2014 | Training Building | 2005-2014 | training_building.osm | Trenton Training B34 | 1 | 1869 | 1869 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 5.2836 | 4.5791 | 4.5791 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Training Bldgs | 0.0002 | 3.5 | 0.879 | 0.8 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Training Building_pre-1960 | Training Building | pre-1960 | training_building.osm | Trenton Training B34 | 2 | 6831 | 6831 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Training Bldgs | 0.0007 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Vehicle Garage_1980-2004 | Vehicle Garage | 1980-2004 | vehicle_garage.osm | B624 | 10 | 12254 | 11811 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 2.6418 | 3.1701 | 3.1701 | 1.7612 | 1.7612 | 1.7612 | 0.31701 | 0.31701 | 0.70447 | 0.31701 | 1.7612 | Hangars | 0.00045 | 3 | 0.879 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Vehicle Garage_pre-1960 | Vehicle Garage | pre-1960 | vehicle_garage.osm | B624 | 3 | 5245.6 | 5220 | 0 | always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }} | always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }} | F:/osruby/Resources/common/BTAP_Construction_Library.osm | Concrete | 1.7612 | 2.1134 | 2.1134 | 1.7612 | 1.7612 | 1.7612 | 0.28179 | 0.28179 | 0.70447 | 0.28179 | 1.7612 | Hangars | 0.0008 | 2.5 | 0.75 | 0.75 | 0.7 | FixedDryBulb | ModulateFlow | 19 | 64000 | 0 | -100 | 1.1 | 1.25 | 1 | 1 | 60 | NA | 0.8 | NA | 82 | 0.8
Note on Z1: Lopez, Phylroy: Used for Hanger doors

## Infiltration Rates
Air Leakage (Infiltration) Rate Assumptions
Units are = m3/s/m2
Infiltration Building Type | 2005-2014 | 1980-2004 | 1960-1979 | pre-1960
Air Terminal | 0.0002 | 0.00035 | 0.0005 | 0.0007
Communications & Control | 0.0002 | 0.00035 | 0.0005 | 0.0007
Control Tower | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fire Hall | 0.0003 | 0.00045 | 0.00075 | 0.0008
Fitness & Rec. - Arena | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Multi-gym | 0.0002 | 0.00035 | 0.0005 | 0.0007
Fitness & Rec. - Pool | 0.0002 | 0.00035 | 0.0005 | 0.0007
Food Services | 0.0002 | 0.00035 | 0.0005 | 0.0007
Hangars | 0.0003 | 0.00045 | 0.00075 | 0.0008
Infrastructure | 0.0003 | 0.00045 | 0.00075 | 0.0008
Medical Facilities | 0.0002 | 0.00035 | 0.0005 | 0.0007
Misc. Bldgs < 100m2 | 0.0002 | 0.00035 | 0.0005 | 0.0007
Mobile Prefab Buildings | 0.0002 | 0.00035 | 0.0005 | 0.0007
Motel Type Residences | 0.0002 | 0.00035 | 0.0005 | 0.0007
Museum | 0.0002 | 0.00035 | 0.0005 | 0.0007
Offices | 0.0002 | 0.00035 | 0.0005 | 0.0007
Recreational / Club Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Religious Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Retail Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Sleeping barracks | 0.0002 | 0.00035 | 0.0005 | 0.0007
Storage Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
Training Bldgs | 0.0002 | 0.00035 | 0.0005 | 0.0007
University Dormitory Type | 0.0002 | 0.00035 | 0.0005 | 0.0007
Warehouses | 0.0003 | 0.00045 | 0.00075 | 0.0008
Workshops | 0.0003 | 0.00045 | 0.00075 | 0.0008
Note on K35: mlubun: ASHRAE 90.1 1999 value
Note on G37: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I37: mlubun: 50% increase in ACH and leakage due to door openings
Note on K37: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M37: mlubun: 50% increase on ACH and leakage due to door openings
Note on G39: mlubun: 50% increase due to hanger door openings
Note on I39: mlubun: 50% increase in ACH and leakage due to door openings
Note on K39: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M39: mlubun: 50% increase on ACH and leakage due to door openings
Note on G45: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I45: mlubun: 50% increase in ACH and leakage due to door openings
Note on K45: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M45: mlubun: 50% increase on ACH and leakage due to door openings
Note on K57: mlubun: ASHRAE 90.1 1999 value
Note on G59: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I59: mlubun: 50% increase in ACH and leakage due to door openings
Note on K59: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M59: mlubun: 50% increase on ACH and leakage due to door openings
Note on G62: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I62: mlubun: 50% increase in ACH and leakage due to door openings
Note on K62: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M62: mlubun: 50% increase on ACH and leakage due to door openings
Note on M69: building renovated in 2005.
Note on G71: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I71: mlubun: 50% increase in ACH and leakage due to door openings
Note on K71: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M71: mlubun: 50% increase on ACH and leakage due to door openings
Note on G72: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I72: mlubun: 50% increase in ACH and leakage due to door openings
Note on K72: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M72: mlubun: 50% increase on ACH and leakage due to door openings
Note on G77: mlubun: 50% increase on ACH and leakage rate due to hanger door openings
Note on I77: mlubun: 50% increase in ACH and leakage due to door openings
Note on K77: mlubun: 50% increase in ACH and leakage rate due to door openings
Note on M77: mlubun: 50% increase on ACH and leakage due to door openings

## Indexes
building_type | building_source | model_file_name
Barracks | B45 | barracks.osm
Fire Hall | Trenton FH B19 | fire_hall.osm
Food Service | B40 | food_service.osm
Hangar | Hangar 4 | hanger.osm
Maintenance Shop | B581 | maintenance_shop.osm
Maintenance Shop-Small | B688 | maintenance_shop_small.osm
Office | B007 | office.osm
Office-Small | B96(Trailer) | office_small.osm
Recreation Center | B720 | recreation_center.osm
Storage Building | B782 | storage_building.osm
Training Building | Trenton Training B34 | training_building.osm
Vehicle Garage | B624 | vehicle_garage.osm
Cold Lake Vintages
1960-1979
1980-2004
2005-2014
pre-1960
BTAP Construction Sets
NA
Concrete
Metal
Boiler Fuel Types
Coal
Diesel
DistrictHeating
Electricity
FuelOil#1
FuelOil#2
Gasoline
NA
NaturalGas
OtherFuel1
OtherFuel2
PropaneGas
SHW Fuel Types
Coal
Diesel
DistrictHeating
Electricity
FuelOil#1
FuelOil#2
Gasoline
NA
NaturalGas
OtherFuel1
OtherFuel2
PropaneGas
Stream

## Equipment_Efficiencies
Reference Info | pre-1960 | 1960-1979 | 1980-2004 | 2005-2014
fan_motor_eff | 0.75 | 0.823 | 0.879 | 0.879
fan_total_eff | 0.75 | 0.75 | 0.75 | 0.8
cop | 2.5 | 2.5 | 3 | 3.5
pump_eff | 0.7 | 0.7 | 0.7 | 0.7
Note on A1: Lopez, Phylroy: Vintage 4 Vintage 3 Vintage 2 Vintage 1 Pre-1960 1960-1979 1980-2004 post-2004 Motor Efficiency 75 (1) 82.3 (2) 87.9 (3) 87.9 (4) Fan Efficiency 75 (5) 75 (5) 75 (5) 80 (5) Pump Efficiency 70 (6) 70 (6) 70 (6) 70 (6) (1) = estimated (2) = average efficiency of “typical” standard efficiency motors as defined in table 12-9 of NEMA MG 1-1993 of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (3) = average efficiency of ASHRAE 90.1 1999 Standard (pg 55) of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (4) = average efficiency of ASHRAE 90.1 2007 Standard (pg 65) of nominal full load efficiency for 4 pole enclosed motors of 1 to 25 hp ratings (5) fan efficiencies depend on the pressure rise and flow and the type of fan. The rated flow will be used for the fan efficiencies for forward curved fans (60-75%), radial fans (69-75%), backward inclined and airfoil fans (75-80%), vane axial (78-85%), tube axial (67-72%), propeller axial (45-50%). Backward inclined fans are the most common in HVAC equipment. (6) pump efficiencies vary by the flow, type of pump and size. For centrifugal pumps, a 2-4 kW motor would have any efficiency of 55-65%, a 5-7.5 kW motor would have an efficiency of 60-70%, a 10-22 kW motor would have an efficiency of 65-75% and a 30-45 kW motor would have an efficiency of 70-80%

## Schedules
schedule_name | schedule_string
always_21C | {"sch":{"name":"always 21", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"21.0", "until":"24:00"} ] } ] } ] }}
always_24C | {"sch":{"name":"always 24", "type":"TEMPERATURE", "period_rules":[ { "start":"Jan-31","end":"Dec-31", "day_rules":[ { "days" :"M,T,W,T,F,S,SN", "hour_rules":[ { "value":"24.0", "until":"24:00"} ] } ] } ] }}
NA | NA